{"text_format":"2","workbook":"xlsx","n_sheets":17,"sheets":["Introduction","Structure Glossary","Mode","Deactivation of residuals","Calcium hypochlorite","Cl-Isocyan","Chlorine dioxide","Hydantoin Products","H2O2","NaOCl","NaOCL Decay","NaOCl-SG","NaOCl-Stab"," NaBr","NH4Br","Peracetic Acid","Stabilized Liquid Halogens"],"not_rendered":{"charts":0,"images":19,"macros":0,"external_links":0,"defined_names":22,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Introduction","index":0,"n_rows":23,"n_cols":1,"rows_kept":23,"cut":false,"hidden":false,"merged":[]}
["BioMatrix, Oxidizers Introduction"]
[]
["The Oxidizer BioMatrix is an Excel Workbook packed with useful information on oxidizing biocides commonly used in recirculating cooling waters.  It is the collaborative effort of the BioMatrix Task Force of the Cooling Water Subcommittee."]
["The biocides included in the Oxidizer BioMatrix have both primary registration and have recirculating cooling water application information on their label.  Biocides for formulation use only or manufacturing use only are not included.  Neither are subregistered biocides."]
[]
[]
["The BioMatrix workbook contains tabs, each representing a table.  The tables are ready to print – no need to highlight the printing area.  The first 3 tabs represent tables containing structure, mode of action and deactivation information.  The next 12 tabs represent tables which include information specific to biocide products.  The biocide products are grouped by chemical composition and activity.  For a given composition and activity, the products are listed alphabetically.  For each biocide product, the following information is covered in its table: common name(s), trade name and manufacturer/supplier, CAS number, EPA registration number, PC Code, chemical composition and activity, the label dose rate, and the label date. Additional information has been inserted where appropriate for the molecule."]
[]
["The BioMatrix is a living document that will be updated periodically to reflect new information on biocide application and to reflect the advent of new biocides and/or the demise of existing biocides."]
[]
["BioMatrix,Oxidizers Acknowledgements"]
["This document has been produced by the AWT Cooling Sub-Committee Biocide Matrix – Oxidizers Task Group by the following individuals:"]
[]
["Task Group Co-Chairs:"]
["Susan P. Rey - The National Colloid Company - Steubenville, Ohio, USA"]
["Farah Azarnia - Albemarle Corporation - Baton Rouge, Louisiana, USA"]
[]
["Task Group Contributors:"]
["Tom Kuechler - Occidental Chemical Corp. - Sauget,Illinois, USA"]
["Amanda Meitz - Biosolutions, LLC - Chagrin Falls, Ohio, USA"]
["Jim Scott - San Joaquin Chemicals, Inc. - Visalia, California, USA"]
["Jeff Kramer - BWA Water Additives - Tucker, Georgia, USA"]
["Ken Sansom - Solutech Water Management, Inc. - Calgary, Alberta, Canada"]

{"sheet":"Structure Glossary","index":1,"n_rows":32,"n_cols":4,"rows_kept":32,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
["Glossary"]
[]
["Common Name","CAS Number","Chemical Name","Structures"]
["Non-Stabilized Oxidizers"]
["Cal hypo","7778-54-3","Calcium hypochlorite","Ca(ClO)2"]
["Chlorine ","7782-50-5","Chlorine ","Cl2"]
["Chlorine dioxide","10049-04-4","Chlorine dioxide","ClO2"]
["Hypo","7681-52-9","Sodium hypochlorite","NaOCl"]
["Ozone","10028-15-6","Ozone"]
["Peroxide","7722-84-1","Hydrogen peroxide","H2O2"]
["Peracetic acid","79-21-0","Peroxyacetic acid"," "]
["Sodium Bromide",null,"Sodium Bromide","NaBr"]
[]
["Stabilized Oxidizers"]
["BCDMH","16079-88-2,  126-06-7, 32718-18-6","1-Bromo-3-chloro-5,5-dimethylhydantoin, 3-Bromo-1-chloro-5,5-dimethylhydantoin, Mixture of the two"]
["DBDMH","77-48-5","1,3-Dibromo-5,5-dimethylhydantoin, 99.4%"]
["DCDMH","118-52-5","1,3-Dichloro-5,5-dimethylhydantoin"]
["DCEMH","89415-87-2","1,3-Dichloro-5-ethyl-5-methylhydantion"]
["Dichlor","2782-57-2","1,3-dichloro-1,3,5-triazinane-2,4,6-trione"]
["MCDMH","6921-17-1","1-Chloro-5,5-dimethylhydantoin"]
["Stabilized Bromine","Mixture","Bromosulfamate and chlorosulfamate"]
["Stabilized Chlorine","Mixture","Chlorosulfamate + NaBr, 6.7% as Cl2"]
["Trichlor","87-90-1","1,3,5-trichloro-1,3,5-triazinane-2,4,6-trione, 100%"]

{"sheet":"Mode","index":2,"n_rows":38,"n_cols":1,"rows_kept":38,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[]
["MODE OF ACTION OF OXIDIZING BIOCIDES"]
[]
["The active biocidal agent is HOCl for all available chlorine donors, including elemental chlorine, and sodium, calcium,"]
["or lithium hypochlorite, the chlorinated isocyanurates, the chlorinated hydantions, and some other chlorinated amines."]
["All of these available chlorine donors product hypochlorous acid (HOCl) by hydrolysis of water.  Since HOCl is a small"]
["neutral molecule, it can readily diffuse thorugh the cell walls of microorganisms.  Other available chlorine species"]
["including hypochlorite ion (OCl-), which are either ionic or larger molecules, can only attack the outside surface"]
["of the cell.  Since HOCl is the same active species for all of these materials, the mode of action of HOCl applies to all"]
["of the available chlorine donors."]
[]
["The effects of chlorine on exposed bacteria, viruses, algae, and other microorganisms include disruption of critical enzymatic"]
["pathways leading to lack of reproduction at lower doses and death at higher doses.  Based on the chemical reactivity"]
["of HOCl, the predominant reaction is oxidation of the thiol (-SH, sulfhydryl) and sulfide (C-S-C) groups in enzymes to"]
["disulfides, sulfoxides, or disulfoxides, thereby destroying the cellular activity of proteins.  HOCl can also have "]
["deleterious effects on DNA or RNA that involve the formation of chlorinated derivatives of nucleotide bases or "]
["interference with DNA and RNA sysnthesis."]
[]
["During treatment with HOCl, bacterial spores lose refractivity, the spore coat separates from the cortex, and lyis"]
["occurs.  In addition, HOCl-treated spores exhibit increased permeability of the spore coat.  Virus inactivation by HOCl"]
["precedes any severe morphological changes, but then virus RNA is degraded into fragments and the virus capsid"]
["is broken down.  Thus, for viruses, HOCl appears to react with the proteins and enzymes as well as the viral RNA."]
[]
["The active biocidal agent for all the available bromine donors in HOBr.  The mode of action is similar to that of HOCl."]
[]
["Monochloramine (NH2Cl) and monobromamine (NH2Br) can also diffuse readily into cells, since they are neutral"]
["molecules and then chlorinate or brominate easily reduced thiol or sulfide groups.  Monochloramine or"]
["monobromamine can be formed by reaction of ammonia or an ammonium salte with the proper amount of any of the"]
["available chlorine or bromine donors, respectively."]

{"sheet":"Deactivation of residuals","index":3,"n_rows":30,"n_cols":6,"rows_kept":30,"cut":false,"hidden":false,"merged":[[11,0,14,12],[17,2,17,5],[29,0,33,12]]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
["Deactivation of residuals of halogen-based oxidizing biocides:"]
[]
["Dehalogenating agents can be used.  Examples of dehalogenating agents are sodium sulfite (Na2SO3), sodium thiosulfate (Na2S2O3), sodium metabisulfite (Na2S2O5), and sodium bisulfite (NaHSO3).   The theoretical dosage (ppm per ppm chlorine) varies depending on the dehalogenating agent.  The dosage of sodium thiosulfate is also dependant on the pH of the system.  Table below contains some dosage information.  Details of the theoretical dosages are in the September 1995 issue of Public Works by Chris Lind. "]
[]
[]
[]
[]
[]
[null,null,"Theoretical Dosage (ppm per ppm Cl2)"]
["Chemical","Formula","pH 4.0","pH 6.5","pH 9.0","pH 11.0"]
["Sodium sulfite","Na2SO3",1.96,1.96,1.96,1.96]
["Sodium thiosulfate","Na2S2O3",2.67,2.23,1.6,1]
["Sodium metabisulfite","Na2S2O5",1.47,1.47,1.47,1.47]
["Sodium bisulfite","NaHSO3*",1.61,1.61,1.61,1.61]
[]
["* Dry Basis"]
[]
[]
["Deactivation of Hydrogen Peroxide:"]
[]
["For continuous waste treatment, the waste peroxide stream may be passed through an open pit or tank containing scrap metal (iron, copper, brass, etc.) which can reduce the H2O2 concentration to an acceptable level before disposal.  For batch treatment, H2O2 can be diluted to 5-10% and a reducing agents, such as sodium bisulfite solution, added to destroy the peroxide.  One pound (0.454 kg) of H2O2 (100%) will be destroyed by approximately 1.9 lb (0.862 kg) of SO3 or its equivalent as bisulfite. (Reference:  E.I du Pont de Nemours & Co. (Inc.) 5/89 literature on storage and handling of Hydrogen Peroxide)."]

{"sheet":"Calcium hypochlorite","index":4,"n_rows":40,"n_cols":15,"rows_kept":40,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[null,"Biocide Selection Table: = Calcium Hypochlorite"]
["Common Name(s)","Trade Name (Manufacturer)*","CAS # ","EPA#","PC\nCode","%\nCaOCl","% Avail.\nCl2","Initial Slug\nDose\n(ppm Product)","Initial Slug\nDose\n(ppm Cl2)#","Subsequent\nSlug Dose\n(ppm Productl)","Subsequent\nSlug Dose\n(ppm Cl2)#","Intermittant\nDose**","Initial\nContinuous\nDose ***","Subsequent\nContinuous\nDose***","Label\nDate"]
["Calcium hypochlorite","Sanuril 110 Tablets\n(Exceltec International Corporation) ","7778-54-3","48482-2",14701,70,"70.0 min","Note 3",null,"Note 3",null,"Note 3","Note 3","Note 3","2011-03-18"]
["Calcium hypochlorite","Calcium Hypochlorite\n(Water Utility Chemicals, Inc.)","7778-54-3","74616-1",14701,68,"65.0 min","Note 4","5-10","Note 4",1,"Note 4","Note 4","Note 4","2011-05-04"]
["Calcium hypochlorite","Calcium Hypochlorite Tablets\n(PPG Industries)","7778-54-3","748-295",14701,68,"65.0 min","7.5-15","5-10","0.75-1.5",1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2011-08-29"]
["Calcium hypochlorite","Chlor Mor Calcium Hypochlorite Granules\n(All Chem Performance Products, Inc.)","7778-54-3","69681-6",14701,68,65,"7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2012-08-21"]
["Calcium hypochlorite","Chlor Mor Calcium Hypochlorite Tablets\n(All Chem Performance Products, Inc.)","7778-54-3","69681-14",14701,68,65,"7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","7.5 ppm Product\n1 ppm free Cl2","2012-06-06"]
["Calcium hypochlorite","ECR Calcium Hypochlorite AST\n(Environmental Compliance Resources, LLC)","7778-54-3","86460-4",14701,68,"65.0 min","7.5-15","5-10","0.75-1.5",1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2011-03-17"]
["Calcium hypochlorite","ECR Calcium Hypochlorite Granules\n(Environmental Compliance Resources, LLC)","7778-54-3","86460-1",14701,68,"65.0 min","7.5-15","5-10","0.75-1.5",1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2011-03-17"]
["Calcium hypochlorite","ECR Calcium Hypochlorite T\n(Environmental Compliance Resources, LLC)","7778-54-3","86460-3",14701,68,"65.0 min","7.5-15","5-10","0.75-1.5",1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2011-08-17"]
["Calcium hypochlorite","HTH Dry Chlorinator Granular\n(Arch Chemicals)","7778-54-3","1258-427",14701,68,"65.0 min","7.5-15",null,1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2011-02-08"]
["Calcium hypochlorite","Pittclor\n(PPG Industries)","7778-54-3","748-217",14701,68,"65.0 min","7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2012-09-05"]
["Calcium hypochlorite","Pittabs\n(PPG Industries)","7778-54-3","748-138",14701,68,"65.0 min","7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2010-04-06"]
["Calcium hypochlorite","Pittabs G-65\n(PPG Industries)","7778-54-3","748-284",14701,68,"65.0 min","7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2011-05-19"]
["Calcium hypochlorite","BioGuard Master Calcium Hypochlorite\n(BioLab, Inc.)","7778-54-3","5185-238",14701,67,null,"Note 2",null,"Note 2",null,"Note 2","Note 2","Note 2","2003-05-29"]
["Calcium hypochlorite","Superchlo\n(Tianjin Pool & Spa Corporation)","7778-54-3","88346-7",14701,67,null,"7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2012-06-20"]
["Calcium hypochlorite","PrimeCLO2\n(F2 Industries, LLC)","7778-54-3","87886-1",14701,65,null,"7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2012-01-13"]
["Calcium hypochlorite","Pro Chlor Granules\n(Global Water Treatment Chemicals)","7778-54-3","87273-1",14701,65,"65.0 min","7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2011-06-20"]
["Calcium hypochlorite","Pro Chlor Tabs\n(Global Water Treatment Chemicals)","7778-54-3","87273-2",14701,65,"65.0 min","7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2011-07-27"]
["Calcium hypochlorite","Super Chlor\n(Jianghan Salt & Chemical Complex)","7778-54-3","74831-20005",14701,65,null,"7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.5 ppm Product\n1 ppm free Cl2","2012-05-29"]
["Calcium hypochlorite","Calcium Hypochlorite Sanitizer Granular 60\n(Arch Chemicals)","7778-54-3","1258-1066",14701,62,"60.0 min","7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","Same as\nSub. Slug","2008-02-01"]
["Calcium hypochlorite","Calcium Hypochlorite Sanitizer Tabs-60\n(Arch Chemicals)","7778-54-3","1258-1064",14701,62,"60.0 min","7.5-15","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","Same as\nSub. Slug","2010-05-25"]
["Calcium hypochlorite","AW07\n(Arch Chemicals)","7778-54-3","1258-1332",14701,53,"51.0 min"," 11-22","5-10",1.5,1,"I: Same\nS: 4oz/10,000 gal\n1 ppm Cl2","Same as\nInitial Slug","2.3 ppm Product\n 1ppm free Cl2","2009-02-10"]
["Calcium hypochlorite","Chlor Mor Cal-Shock SWB\n(All Chem Performance Products) ","7778-54-3","69681-28",14701,52.4,"45.0 min"," 11-22","5-10",1.5,1,"Same as Slug Doses","Same as\nInitial Slug","2.3 ppm Product\n 1ppm free Cl2","2009-11-25"]
["Calcium hypochlorite","AW08\n(Arch Chemicals)","7778-54-3","1258-1333",14701,47.6,"45.0 min","Note 1","5-10","Note 1",1,"Same as Slug Doses","Same as\nInitial Slug","Same as\nSub. Slug","2009-05-19"]
["Calcium hypochlorite","AW09\n(Arch Chemicals)","7778-54-3","1258-1334",14701,47.1,"45.0 min"," 11-22","5-10","Note 1",1,"Same as Slug Doses","Same as\nInitial Slug","Note 1","2011-07-28"]
[]
["*PAN Pesticides Database-Chemicals                                              I: Initial   S: Subsequent"]
["**Apply half (or 1/3, 1/4, or 1/5) of the initial or maintenance dose when half (or 1/3, 1/4, or 1/5) of the water has been blown down."]
["***Dose: oz Product fed per listed gallons of blowdown                    # ppm Free Cl2"]
["Notes: 1. I: Use feed dispenser & test kit to hit 5-10 ppm Cl2.  S: Use feed dispenser & test kit to hit 1 ppm Cl2.  2. Close bleed valve.  Add 15-30 ppm Product, wait 10 min, then measure Cl2.  If <3 ppm repeat.         "]
["3. Refer to Exceltec or Eltech feeder instructions.  Note: A dose of 9.6 ppm Product yields 6 ppm Cl2.  4. I: Use feed dispenser & test kit to hit 5-10 ppm Cl2.  S: Repeat targeting 1 ppm Cl2."]

{"sheet":"Cl-Isocyan","index":5,"n_rows":48,"n_cols":12,"rows_kept":48,"cut":false,"hidden":false,"merged":[[10,6,11,6],[10,10,11,10],[10,11,11,11],[10,0,11,0],[10,1,11,1],[10,2,11,2],[10,3,11,3],[10,4,11,4],[10,5,11,5],[10,7,11,7]]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: = Chlorinated Isocyanurates"]
["Common\nName","Trade Name (Manufacturer)*","CAS No.","EPA Reg. No.","PC Code","Canadian Reg. No.","% Isocy-\nanurate","% Av.\nCl2","Slug & Continuous","Slug & Continuous","State Reg.","Label\nDate"]
[{"$nulls":8},"(ppm Product/\nppm Total Cl2)","Target\nppm Cl2**"]
["Dichlor","ACL 60 EUP Chlorinating Granules\n(Occidental Chemical Corp)","2893-78-9","935-41",81404,null,97,62,"I: 18-90; S: 3.6-18/\nI: 11-56; S: 2.2-11","I: 0.5-10 Av. Cl2\nS: 0.5-1.0 Av. Cl2",null,"2010-05-19"]
["Dichlor","Clor Mor Chlorinating Granules\n(AllChem Performance Products, Inc.)","2893-78-9","69681-3",81404,null,99,63,"15-30/\n9.5-18.9",null,"***","2008-06-04"]
["Dichlor","Clor Mor 60 PG\n(AllChem Performance Products Inc.)","2893-78-9","69681-26",81404,null,99,62,"I: 18-90; S: 3.6-18/\nI: 11-56; S: 2.2-11","I: 0.5-10 Av. Cl2\nS: 0.5-1.0 Av. Cl2","***","2008-07-14"]
["Dichlor","NEO CHLOR SDIC GRANULES\n(Shikoku International Corp)","2893-78-9","72139-5",81404,null,99,62,"I: 18-90; S: 3.6-18/\nI: 11-56; S: 2.2-11","I: 0.5-10 Av. Cl2\nS: 0.5-1.0 Av. Cl2","***","2008-07-14"]
["Dichlor","Towerchlor 60 Granules\n(Occidental Chemical Corp)","2893-78-9","935-69",81404,null,97,62,"I: 18-90; S: 3.6-18/\nI: 11-56; S: 2.2-11","I: 0.5-10 Total Cl2\nS: 0.5-1.0 Total Cl2",null,"2010-12-17"]
[]
["Dichlor\ndihydrate","ACL 56 EUP Chlorinating Granules\n(Occidental Chemical Corp)","51580-86-0","935-42",81407,null,99,55,"I: 18-90; S: 3.6-18/\nI: 9.9-50; S: 2.0-9.9","I: 0.5-10 Av. Cl2\nS: 0.5-1.0 Av. Cl2",null,"2011-11-01"]
["Dichlor\ndihydrate","Betz Entec 362\n(GE Betz Inc)","51580-86-0","34571-14",81407,null,99,55,"I: 12-180; S:6-102/\nI: 6.6-99; S: 3.3-56","≤1 Free Cl2",null,"2011-06-21"]
["Dichlor\ndihydrate","CDB Clearon Granular\n(Clearon Corp)","51580-86-0","69470-20",81407,null,99,55.5,"I: 7.5-9.7; S: 0.75-2.2/\nI: 4.1-5.3; S: 0.41-1.2","I: 0.5-1.0 Free  Cl2\nS: 0.5-1.0 Free Cl2","***","2011-06-02"]
["Dichlor\ndihydrate","Clor Mor Diclor 56\n(AllChem Performance Products, Inc.)","51580-86-0","69681-8",81407,null,99,null,null,"≤ 3 Cl2, Free","***","2008-06-04"]
["Dichlor\ndihydrate","Clor Mor 56 PG\n(AllChem Performance Products, Inc.)","51580-86-0","69681-25",81407,null,99,55,"I: 18-90; S: 3.6-18/\nI: 9.9-50; S: 2.0-9.9","I: 0.5-10 Av. Cl2\nS: 0.5-1.0 Av. Cl2","***","2008-07-14"]
["Dichlor\ndihydrate","Neo Chlor DICD Granules\n(Shikoku International Corp)","51580-86-0","72139-4",81407,null,99,55,"I: 18-90; S: 3.6-18/\nI: 9.9-50; S: 2.0-9.9","I: 0.5-10 Av. Cl2\nS: 0.5-1.0 Av. Cl2","***","2008-07-14"]
["Dichlor\ndihydrate","Towerchlor 56 Granules\n(Occidental Chemical Corp)","51580-86-0","935-68",81407,25822,99,56,"I: 18-90; S: 3.6-18/\nI: 9.9-50; S: 2.0-9.9","I: 0.5-10 Total Cl2\nS: 0.5-1.0 Total Cl2",null,"2010-05-11"]
[]
["Trichlor","BioGuard Master Trichloro\nCompacted (Bio-Lab, Inc.)","87-90-1","5185-144",81405,null,99,90,"I: 7.5/6.75","I:1.0-2.0; Int: 1.0;\nC: 0.5-1.0 Free Cl2","***","2011-07-14"]
["Trichlor","CDB-90 3\" Chlorinating Tablets\n(Clearon Corp)","87-90-1","69470-19",81405,null,99,90,"I: 6.0; M: 0.60-1.2/\nI: 5.4; M: 0.54-1.1","I: 0.5-1.0 Free Cl2\nM: 0.5-1.0 Free Cl2","***","2013-01-23"]
["Trichlor","Chemical Treatment C-2185\n(ChemTreat, Inc.)","87-90-1","15300-21",81405,null,99,89,"I: 6.0; M: 0.60-1.2/\nI: 5.4; M: 0.54-1.1","I: 0.5-1.0 Free Cl2\nM: 0.5-1.0 Free Cl2",null,"2004-11-10"]
["Trichlor","Clor Mor 90 PT\n(AllChem Performance Products, Inc.)","87-90-1","69681-22",81405,null,98.25,90,"I: 12-60; S: 2.4-12/\nI:11-54; S: 2.2-11","I: 0.5-10 Av. Cl2\nS: 0.5-1.0 Av. Cl2\nBoth Int. and C","***","2008-03-31"]
["Trichlor","Clor Mor Trichlor Compacted\n(AllChem Performance Products, Inc.)","87-90-1","69681-15",81405,null,98.6,90,"I: 7.5/6.75","I:1.0-2.0; Int: 1.0;\nC: 0.5-1.0 Free Cl2",null,"2012-10-25"]
["Trichlor","Cooling Tower Chlorinating Tablets\n(N. Jonas)","87-90-1","3432-78",81405,null,99,90,"I: 12-60; S: 2.4-12/\nI:11-54; S: 2.2-11","I: 0.5-1.0 Total Cl2\nM: 0.5-1.0 Total Cl2\nBoth Int. and C","***","2003-01-22"]
["Trichlor","Towerchlor 90 Tablets\n(Occidental Chemical Corp)","87-90-1","935-72",81405,22096,99.4,90,"I: 12-60; S: 2.4-12/\nI:11-54; S: 2.2-11","I: 0.5-1.0 Total Cl2\nM: 0.5-1.0 Total Cl2\nBoth Int. and C",null,"2010-05-19"]
["Trichlor","Towerpro Tablets\n(BWA Water Additives US LLC)","87-90-1","83451-1",81405,null,99,90,"I: 7.5/6.75","I:1.0-2.0; Int: 1.0;\nC: 0.5-1.0 Av. Cl2","***","2009-07-13"]
[]
["Dichlor\n+ NaBr","Towerbrom 60M Granules\n(Occidental Chemical Corp)","2893-78-9\n7647-15-6","935-71","81404\n13907",27275,"90.00% Dichlor\n7.00% NaBr","57.00\n","I: 18-90; S: 3.6-18/\nI: 10-51: S: 2.1-10","I: 0.5-10 Total as Cl2;\nS: 0.5-1.0 Total as Cl2\nBoth Int. and C",null,"2010-05-19"]
[]
["Trichlor\n+ BCDMH","Bromoblend 99\n(ICL-IP America Inc.)","87-90-1\n126-06-7","8622-77","81404\n6322",null,"29.70% Trichlor\n68.60% BCDMH","67.30\n","I:20-60; S: 9.6-30/\nI: 13-40; S: 6.5--20","I: 0.44 as Free Cl2\n(1.0 as Free Br2)\nM: Same as for I","***","2010-06-11"]
[]
["Trichlor\n+ NaBr","Towerbrom 90M Tablets\n(Occidental Chemical Corp)","87-90-1\n7647-15-6","935-75","81405\n13907",25930,"92.90% Trichlor\n6.90% NaBr","83.00","I: 12-60: S: 2.4-12/\nI: 10-50: S: 2.0-10","I: 0.5-1.0 Total Cl2\nM: 0.5-1.0 Total Cl2\nBoth Int. and C",null,"2010-08-11"]
["Trichlor\n+ NaBr","Towerbrom 9010 Tablets\n(Occidental Chemical Corp)","87-90-1\n7647-15-6","935-78","81405\n13907",null,"89.90% Trichlor\n9.90% NaBr",null,"I: 12-60: S: 2.4-12/\nI: 10-50: S: 2.0-10","I: 0.5-1.0 Total Cl2\nM: 0.5-1.0 Total Cl2\nBoth Int. and C",null,"2010-05-19"]
["*PAN Pesticides Database-Chemicals                                           ",null,"** I = initial  dose.  S = subsequent dose.  ",null,null,null,"***No state registrations for cooling tower use"]
["Notes:",{"$nulls":5},"#: I = Initial.  Int. = Intermittant.  C = Continuous.  M = Maintenance"]
["Trichlor = trichloro-s-triazinetrione (CAS No. 87-90-1), also called trichloroisocyanuric acid"]
["Dichlor = sodium dichloro-s-triazinetrione (CAS No. 2893-78-9), also called sodium dichloroisocyanurate"]
["Dichlor dihydrate = sodium dichloro-s-triazinetrione dihydrate (CAS No. 51580-86-0), also called sodium dichloroisocyanurate dihydrate"]
["NaBr = sodium bromide (CAS No. 7647-15-6)"]
["BCDMH = 3-bromo-1-chloro-5,5-dimethylhydantoin (CAS No. 126-06-7)",null,null,null,"Many of the product names listed are registered trademarks."]

{"sheet":"Chlorine dioxide","index":6,"n_rows":65,"n_cols":11,"rows_kept":65,"cut":false,"hidden":false,"merged":[[10,10,11,10],[10,5,11,5],[10,9,11,9],[10,0,11,0],[10,1,11,1],[10,2,11,2],[10,3,11,3],[10,4,11,4],[10,6,11,6]]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: = Chlorine Dioxide / Sodium Chlorite / Sodium Chlorate"]
["Common name","Trade Name (Manufacturer)","CAS No.","EPA Reg. No.","PC Code","Canadian Reg. No.","Percent Active Ingredient","Cooling Water Dose","Residual","Comments","Label\nDate"]
[{"$nulls":7},"(ppm)** (as ClO2 unless specified otherwise)","(ppm as ClO2)**"]
["Chlorine Dioxide\n(ClO2)","Anthium Dioxcide\n(International Dioxide Inc)","10049-04-4","9150-2",20503,null,"5% ClO2","I = 5 - 20","I = 5 - 20","Must activate by adding\nacid to generate free ClO2.","2011-03-18"]
["Chlorine Dioxide\n(ClO2)","ProOxine\n(Bio-Cide Iinternational Inc)","10049-04-4","9804-9",20503,null,"5% ClO2","I = 5\nM = Not Given","Not Given","Must activate by adding\nacid to generate free ClO2.","2012-06-12"]
["Chlorine Dioxide\n(ClO2)","CARNEBON 200                                    (International Dioxide Inc)","10049-04-4","9150-3",20503,null,"2% ClO2","I = 5 - 20","Not Given","Must activate by adding\nacid to generate free ClO2.","2005-09-14"]
["Chlorine Dioxide\n(ClO2)","OXINE\n(Bio-Cide Iinternational Inc)        ","10049-04-4","9804-1",20503,null,"2% ClO2","I = 5\nM = Not Given","Not Given","Must activate by adding\nacid to generate free ClO2.","2012-06-19"]
["Chlorine Dioxide\n(ClO2)","SaniCide-2                                              (ConSeal International Inc)","10049-04-4","58300-19",20503,null,"2% ClO2","I = 2.5 gal/10,000 gal","Not Given","Must activate by adding\nacid to generate free ClO2.","2010-08-24"]
["Chlorine Dioxide\n(ClO2)","CDG Solution 3000                                (CDG Envionmental LLC)","10049-04-4","75757-2",20503,null,"0.3% ClO2","I = 50\nM = 5","Not Given","Ready to use liquid.\n3000 ppm ClO2 in water.","2011-09-13"]
[]
["Sodium chlorate (ClO2 precursor)","Purate\n(EKA Chemicals Inc)","7775-09-9","49620-4",73301,29887,"40% NaClO3","Use in a ClO2 generator","I = 0.1 - 5\nM = 0.1 - 1","Registered in Canada,\nbut no cooling tower use.","2011-06-06"]
["Sodium chlorate (ClO2 precursor)","DREW 3025                                      (Hercules Inc (Ashland Inc))","7775-09-9","74655-28",73301,25632,"25% NaClO3","Use in a ClO2 generator","I = 0.1 - 5\nM = 0.1 - 1","Registered in Canada,\nbut no cooling tower use.","2010-09-29"]
[]
["Sodium chlorite* (ClO2 precursor)","Sodium Chlorite - Precursor for Chlorine Dioxide Solution Pack\nICA TriNova LLC)","7758-19-2","79814-3",20502,null,"80% NaClO2","Use in a ClO2 generator\nFor algae control*\nI= 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given",null,"2007-05-17"]
["Sodium chlorite (ClO2 precursor)","Sodium Chlorite Technical 80 Pct             (SAF-T-CHLOR GRANULAR)                   (Ercros SA)","7758-19-2","52564-1",20502,null,"80% NaClO2    (Dry Basis)","Use in a ClO2 generator","Not Specified",null,"2006-08-01"]
["Sodium chlorite* (ClO2 precursor)","Technical Sodium Chlorite                     (Occidental Chemical Corp)","7758-19-2","5382-42",20502,null,"80% NaClO2","Use in a ClO2 generator\nFor algae control*\nI = 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given",null,"2009-12-30"]
["Sodium chlorite (ClO2 precursor)","TwinOxide COMPONENT A                      (TwinOxide International BV)","7758-19-2","86054-1",20502,null,"64% NaClO2 ","I = 0.5 - 1\nM = 0.1-0.2      ","Not Given","Must mix with Compo-\nnent B before dosing.","2009-12-08"]
["Sodium chlorite (ClO2 precursor)","AO2 COMPONENT A                              (Applied Oxidation LLC)","7758-19-2","88800-1",20502,null,"52% NaClO2 ","I = 0.1 - 5\nM = 0.1 - 1","I = 0.1 - 5\nM = 0.1 - 1","Must mix with Compo-\nnent B before dosing.","2012-04-16"]
["Sodium chlorite (ClO2 precursor)","APPOX D-3000 COMPONENT A              (Applied Oxidation LLC)","7758-19-2","88800-2",20502,null,"52% NaClO2 ","I = 0.5 - 1\nM = 0.1 - 0.2","I = 0.5 - 1\nM = 0.1 - 0.2","Must mix with Compo-\nnent B before dosing.","2012-05-01"]
["Sodium chlorite* (ClO2 precursor)","Technical Sodium Chlorite Solution 50    (Occidental Chemical Corp)","7758-19-2","5382-41",20502,null,"37% NaClO2","Use in a ClO2 generator\nFor algae control*\nI = 19 (as NaClO2)\nM = 9 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given","1 gal = 11.62 lb\n1 gal = 4.3 lb NaClO2","2009-12-30"]
["Sodium chlorite (ClO2 precursor)","TowerGUARD                                           (ODORSTAR LLC)","7758-19-2","72874-2 (87508-1)",20502,null,"32% NaClO2","Not Specified","I = 0.5 - 1\n M = 0.1 - 0.2","A 75 g pouch in 3000 gal gives 0.3-0.4 ppm ClO2","2004-08-05"]
["Sodium chlorite* (ClO2 precursor)","31% Active Sodium Chlorite Solution         (Occidental Chemical Corp)","7758-19-2","5382-45",20502,null,"31% NaClO2","Use in a ClO2 generator\nFor algae control*\nI = 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given","1 gal = 10.65 lb\n1 gal = 3.3 lb NaClO2","2009-12-30"]
["Sodium chlorite* (ClO2 precursor)","Electrolite 31                                           (PureLine Treatment Systems)","7758-19-2","72852-4",20502,null,"31% NaClO2","Use in a ClO2 generator\nFor algae control*\nI = 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given","1 gal = 3.3 lb NaClO2","2011-09-28"]
["Sodium chlorite (ClO2 precursor)","Selectrocide 5G                                     (Selective Micro Technologies LLC)","7758-19-2","74986-5",20502,null,"30.5% NaClO2","I = 5+\nM = 0.5+","I = 5\nM = 0.5",null,"2010-07-10"]
["Sodium chlorite (ClO2 precursor)","Selectrocide 2L500                                  (Selective Micro Technologies LLC)","7758-19-2","74986-4",20502,null,"30.5% NaClO2","I = 5+\nM = 0.5+","I = 5\nM = 0.5",null,"2011-12-14"]
["Sodium chlorite (ClO2 precursor)","ADOX 3125                                     (International Dioxide Inc)","7758-19-2","9150-7",20502,29850,"25% NaClO2","Use in a ClO2 generator","0.25 - 5",null,"2009-09-18"]
["Sodium chlorite (ClO2 precursor)","AKTA KLOR 25                                       (Occidental Chemical Corp)","7758-19-2","21164-6 ",20502,null,"25% NaClO2 ","Use in a ClO2 generator","0.25 - 5",null,"2009-12-30"]
["Sodium chlorite (ClO2 precursor)","CLOSURE CENTRAL 25                      (CLOSURE CENTRAL PM in Canada)   (JohnsonDiversey, Inc)","7758-19-2","70627-55",20502,28674,"25% NaClO2","Use in a ClO2 generator","I = 0.3 - 1.5\nM = up to 1\nFor algae = 5 ","1 gal = 2.58 lb NaClO2","2006-09-13"]
["Sodium chlorite (ClO2 precursor)","DREWCHLOR 4107M                       (DREWCHLOR 4107 in Canada)            (Hercules Inc (Ashland Inc))","7758-19-2","74655-26 (1757-96)",20502,24807,"25% NaClO2","Use in a ClO2 generator","I = 0.1 - 5\nM = 0.1 - 1","1 gal = 2.58 lb NaClO2","2012-05-21"]
["Sodium chlorite* (ClO2 precursor)","ElectroLite 25\n(Purecide 25 in Canada)\n(PureLine Treatment Systems)","7758-19-2","72852-3",20502,28854,"25% NaClO2","Use in a ClO2 generator\nFor algae control*\nI= 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given","1 gal = 2.58 lb NaClO2","2012-01-08"]
["Sodium chlorite (ClO2 precursor)","ERCOPURE 25                                      (Sodium Chlorite Solution 25 in Canada)  (ERCO Worldwide)","7758-19-2","53345-14",20502,24802,"25% NaClO2","Use in a ClO2 generator","0.25 - 5",null,"2010-07-08"]
["Sodium chlorite (ClO2 precursor)","SABRECHLOR 25                                  (SABRE Oxidation Technologies Inc)","7758-19-2","73139-1",20502,null,"25% NaClO2","Use in a ClO2 generator","0.25 - 5",null,"2003-11-14"]
["Sodium chlorite* (ClO2 precursor)","SaniCide-20                                           (ConSeal International Inc)","7758-19-2","58300-18",20502,null,"25% NaClO2 ","Use in a ClO2 generator\nFor algae control*\nI = 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given","1 gal = 2.58 lb NaClO2","2011-11-02"]
["Sodium chlorite* (ClO2 precursor)","Technical Sodium Chlorite Solution 31.25 (Occidental Chemical Corp)","7758-19-2","5382-43",20502,26203,"25% NaClO2","Use in a ClO2 generator\nFor algae control*\nI = 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given","1 gal = 10.38 lb\n1 gal = 2.58 lb NaClO2","2010-01-27"]
["Sodium chlorite (ClO2 precursor)","ADOX 1875                                              (International Dioxide Inc)","7758-19-2","9150-13",20502,null,"15% NaClO2 ","Use in a ClO2 generator","0.25 - 5",null,"2012-04-02"]
["Sodium chlorite* (ClO2 precursor)","Aqua-Clear 15                                        (CH2O Inc)","7758-19-2","43553-34",20502,null,"15% NaClO2 ","Use in a ClO2 generator\nFor algae control*\nI = 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given","1 gal =  1.55 lb NaClO2","2010-08-11"]
["Sodium chlorite* (ClO2 precursor)","CLEAN FINISH                                       (CH2O Inc)","7758-19-2","43553-35",20502,null,"15% NaClO2 ","Use in a ClO2 generator\nFor algae control*\nI = 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given","1 gal =  1.55 lb NaClO2","2010-08-11"]
["Sodium chlorite (ClO2 precursor)","SODIUM CHLORITE SOLUTION 15           (ERCO Worldwide)","7758-19-2","53345-20",20502,null,"15% NaClO2","Use in a ClO2 generator","0.25 - 5",null,"2011-08-15"]
["Sodium chlorite* (ClO2 precursor)","Technical Sodium Chlorite Solution 18.75 (Occidental Chemical Corp)","7758-19-2","5382-44",20502,null,"15% NaClO2","Use in a ClO2 generator\nFor algae control*\nI = 20 (as NaClO2)\nM = 10 (as NaClO2) ","I = 0.1 - 5\nM = 0.1 - 1\nNot Given","1 gal = 10.33 lb\n1 gal =  1.55 lb NaClO2","2009-12-30"]
["Sodium chlorite (ClO2 precursor)","DURA KLOR                                          (Occidental Chemical Corp)","7758-19-2","21164-3 ",20502,null,"8.3% NaClO2 ","I = 9 (as NaClO2)","Not Given","Must activate by adding\nacid to generate free ClO2.","2009-12-30"]
["Sodium chlorite (ClO2 precursor)","SC-8\n(CHL LLC)","7758-19-2","87134-2",20502,null,"8.3% NaClO2 ","I = 5","Not Given",null,"2010-07-14"]
["Sodium chlorite (ClO2 precursor)","ADOX 750                                              (International Dioxide Inc)","7758-19-2","9150-8",20502,null,"7.5% NaClO2 ","Use in a ClO2 generator","0.25 - 5",null,"2012-01-09"]
["Sodium chlorite (ClO2 precursor)","AKTA KLOR 7.5                                       (Occidental Chemical Corp)","7758-19-2","21164-9 ",20502,null,"7.5% NaClO2 ","Use in a ClO2 generator","0.25 - 5",null,"2009-12-30"]
["Sodium chlorite (ClO2 precursor)","GENEROX 750                                       (Hercules Inc (Ashland Inc))","7758-19-2","74655-30 (1757-315)",20502,null,"7.5% NaClO2","Use in a ClO2 generator","0.25 - 5",null,"2009-10-30"]
["Sodium chlorite (ClO2 precursor)","SODIUM CHLORITE SOLUTION 7.5          (ERCO Worldwide)","7758-19-2","53345-19",20502,null,"7.5% NaClO2","Use in a ClO2 generator","0.25 - 5",null,"2011-08-18"]
["Sodium chlorite (ClO2 precursor)","SC-5                                                      (CHL LLC)","7758-19-2","87134-1",20502,null,"7.3% NaClO2 ","I = 5","Not Given",null,"2010-04-06"]
[]
["Sodium chlorite + Dichlor Dihydrate","Aseptrol G-Tab10                                   (BASF Corporation)","7758-19-2   51580-86-0","70060-16","20502       81407",null,"20% NaClO2 +\n8% Dichlor Dihydrate","I = 3 - 66 (as product)","I = 0.1 - 0.5\nM = 0.1",null,"2008-08-07"]
["Sodium chlorite + Dichlor Dihydrate","Aseptrol PW                                         (BASF Corporation)","7758-19-2    51580-86-0","70060-33","20502   81407",null,"20.8% NaClO2 +\n7% Dichlor Dihydrate","I = 10 - 250 g/1000 gal\nM = 10 - 50 g/1000 gal","I = 0.1 - 0.5\nM = 0.1 - 0.5",null,"2012-01-13"]
[]
["* NaClO2 is a much less active biocide than ClO2, but dissipates much more slowly. ",{"$nulls":5},"Labels that have not been updated since 2002 are not listed, since they are probably obsolete."]
["** I = Initial (Slug) Dose.  M = Maintainence (Continuous) Dose.  (ppm = mg/L)",{"$nulls":5},"Many of the product names listed are registered trademarks."]
["ClO2 = Chlorine Dioxide (CAS No. 10049-04-4)"]
["NaClO2 = Sodium Chlorite (CAS No. 7758-19-2) is a precursor for ClO2."]
["NaClO3 = Sodium Chlorate (CAS No. 7775-09-9) is a precursor for ClO2."]
["Dichlor Dihydrate = Sodium Dichloro-s-triazinetrione Dihydrate (CAS No. 51580-86-0), also called Sodium Dichloroisocyanurate Dihydrate."]

{"sheet":"Hydantoin Products","index":7,"n_rows":39,"n_cols":13,"rows_kept":39,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: = Halohydantoins"]
["Common Name(s)","Trade Name                           (Manufacturer)*","CAS #**","EPA#","PC Code","PMRA # (Canada)","Composition***","% Av Br2","% Av Cl2","% Total Av. Halogen as Cl2","Cooling Water\nDose (ppm)#","Target halogen residual, ppm","Label\nDate"]
["BCDMH","BCDMH TABS\n(Enviro Tech Chem. Services, Inc)","16079-88-2","63838-4",6315,null,"BCDMH, 98.0%",null,null,null,"I:  24-72; M:  12-36","at least 1 ppm \"active\" Br2 for at least 4 hrs","2006-12-07"]
["BCDMH","HALOGENE G\n(ICL-IP America, Inc.)","32718-18-6 or 16079-88-2 ","8622-29",6315,null,"BCDMH, 98.0%",null,null,null,"I:  24-72; M:  12-36","1 ppm \"active\" Br2 for at least 4 hrs","2011-10-11"]
["BCDMH","HALOGENE T-30\n(ICL-IP America, Inc.)","32718-18-6 or 16079-88-2 ","8622-30",6315,null,"BCDMH, 98.0%",null,null,null,"I:  24-72; M:  12-36","1 ppm \"active\" Br2 for at least 4 hrs"," 07/18/11"]
["BCDMH","Dantoin BCDMH RW tablets\n(Lonza Inc.)","16079-88-2\n32718-18-6","6836-317",6315,null,"BCDMH, 97.7%",64.73,28.72,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2009-12-17"]
["BCDMH","BIOGUARD MASTER BCDMH\n(Bio-Lab Inc.)","16079-88-2","5185-420",6315,null,"BCDMH, 96.0%",null,null,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2011-09-27"]
["BCDMH","BIOLAB BCDMH GRANULAR\n(Bio-Lab Inc.)","16079-88-2","5185-490",6315,null,"BCDMH, 96.0%",null,null,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2004-10-05"]
["BCDMH","BIO-TROL 88-p\n(GE Betz, Inc)","16079-88-2","3876-150",6315,null,"BCDMH, 96.0%",60,28,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2011-06-21"]
["BCDMH","BromiCide Granules\n(BWA Water Additives US LLC)","16079-88-2","83451-3",6315,19351,"BCDMH, 96.0%",null,null,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2009-07-07"]
["BCDMH","BromiCide Powder\n(BWA Water Additives US LLC)","16079-88-2","83451-12",6315,null,"BCDMH, 96.0%",null,null,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2011-01-03"]
["BCDMH","BromiCide Tablets\n(BWA Water Additives US LLC)","16079-88-2","83451-4",6315,19355,"BCDMH, 96.0%",null,null,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2006-08-03"]
["BCDMH","CLOR MOR BROMINATING TABLETS\n(Allchem Performance Products, Inc.)","16079-88-2","69681-16",6315,null,"BCDMH, 96.0%",null,null,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2009-06-02"]
["BCDMH","GBCH\n(Buckman)","32718-18-6","1448-428",6315,null,"BCDMH, 96.0%",null,null,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2011-06-20"]
["BCDMH","HALOGENE B22\n(ICL-IP America, Inc.)","32718-18-6 or 16079-88-2 ","8622-28",6315,null,"BCDMH, 96.0%",null,null,null,"I:  24-72; M:  12-36","1 ppm \"active\" Br2 for at least 4 hrs","2010-06-11"]
["BCDMH","TBCH\n(Buckman)","16079-88-2","1448-420",6315,null,"BCDMH, 96.0%",null,null,null,"I:  24-72; M:  12-36","1-3 ppm Br2 for at least 4 hrs","2010-04-23"]
["BCDMH","Aquate\n(BWA Water Additives US LLC)","16079-88-2","83451-10",6315,27065,"BCDMH, 40.0%",26.5,11.9,null,"I: 47.7-143 ppm by volume; M:  23.8-72 ppm by volume","1-3 ppm Br2 for at least 4 hrs","2009-07-13"]
["BCDMH","BromiCide Gel\n(BWA Water Additives US LLC)","16079-88-2","83451-11\n5185-487",6315,28062,"BCDMH, 35.0%",23.2,10.4,null,"I:  54.5-163.4 ppm by volume; M:  27.2-82.3 ppm by volume","1-3 ppm Br2 for at least 4 hrs"," 08/15/03"]
["BCDMH + DBDMH","AquaBasics Brominating Tablets\n(Mid-Continent Packaging Inc.)","16079-88-2\n77-48-5 ","66397-1","6315\n\n6317",null,"BCDMH, 86.4%;      DBDMH, 8.6%",66.8,25.4,null,"Intermittent:  I: 12-120; M: 12-90; Continuous: I: 12-120; M: 12-90",null,"2010-07-26"]
["BCDMH DCDMH","Dantochlor RW\n(Lonza Inc.)","118-52-5\n89415-87-2","6836-113","28501\n\n128826","20902 (D-RW Briquettes Microbiocide) and 25261 (D-RW Granular Microbiocide)","BCDMH, 81.1%\nDCDMH,16.1%",null,68,68,"Intermittent:  I: 12-120; M: 12-90; Continuous: I: 12-120; M: 12-90",null,"2009-12-16"]
["BCDMH+ DCDMH + DCEMH","Dantobrom RW\n(Lonza Inc.)  ","16079-88-2\n118-52-5\n89415-87-2","6836-115","6315\n28501\n128826",null,"BCDMH, 54.2%\nDCDMH, 28.9%\nDCEMH, 15.9%",null,null,62.8,"Intermittent:  I: 12-120; M: 12-90; Continuous: I: 12-120; M: 12-90","The composition on the label is different from Lonza's technical literature","2011-10-11"]
["BCDMH + Trichlor","BROMOBLEND 99\n(ICL-IP America, Inc.)","32718-18-6\n87-90-1","8622-77","6315\n81405",null,"BCDMH, 68.6%;     Trichloro, 29.7%",null,null,67.3,"I:  20-60; M:   9.5-30","1 ppm \"active\" Br2 for at least 4 hrs","2010-06-11"]
["CDMH MCDMH","MCDMH-EUP\n(Lonza Inc.)","6921-17-1, 118-52-5","6836-324","28500\n28501",null,"CDMH, 90.025%\nDBDMH, 8.675%",null,44.6,null,"Intermittent:  I: 12-120; M: 12-90; Continuous: I: 12-120; M: 12-90",null,"2007-07-05"]
["DBDMH","XtraBrom 111 Biocide\n(Albemarle)","77-48-5","3377-62",6317,null,"DBDMH, 99.4%",111,null,49,"Approx. 3.7 ppm\nproduct yields a\ntheoritical 4 ppm\navailable Br2 in a\ndemand-free system.","0.5-5 ppm as Br2","2008-11-20"]
["DBDMH","XtraBrom T\n(Albemarle)","77-48-5","3377-62",6317,null,"DBDMH, 99.4%",111,null,49,"Approx. 3.7 ppm\nproduct yields a\ntheoritical 4 ppm\navailable Br2 in a\ndemand-free system.","0.5-5 ppm as Br2","2008-11-20"]
[]
["*NPIRS Database",null,null,"***% active",{"$nulls":4},"Note: 2.25 X mg/L as Cl2 = mg/L as Br2"]
["**  CAS number from product MSDS or PAN database",null,null,"#   I: Initial Dose; M: Maintenance Dose, both as product"]
["BCDMH:","1-Bromo-3-chloro-5,5-dimethylhydantoin"]
["DBDMH:","1,3-Dibromo-5,5-dimethylhydantoin",null,"DCEMH:","1,3-Dichloro-5-ethyl-5-methylhydantoin",null,null,"Trichlor:","Trichloro-s-triazinetrione",null,"CDMH:","1-Chloro-5,5-dimethylhydantoin"]

{"sheet":"H2O2","index":8,"n_rows":16,"n_cols":9,"rows_kept":16,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: Hydrogen Peroxide"]
[]
["Common Name(s)","Trade Name (Manufacturer)*","CAS #","EPA#","PC Code","% H2O2","Slug/Intermittant Dose (ppm)*","Continuous                 Dose (ppm)*","Label\nDate"]
["Hydrogen Peroxide","B-Cap 35 Antimicrobial Agent (FMC)","7722-84-1","72372-1",595,35,"I: 26-1438 as product\n10-500 as H2O2\nM: 8.8-274 as product\n3-100 as H2O2","I: 26-1438 as product\n10-500 as H2O2\nM: 2.6-141 as product\n1.0-50 as H2O2","2011-01-05"]
["Hydrogen Peroxide","B-Cap 27 Antimicrobial Agent (FMC)","7722-84-1","72372-4",595,27,"I: 34-1839 as product\n10-500 as H2O2\nM: 8.6-265 as product\n3-100 as H2O2","I: 34-1839 as product\n10-500 as H2O2\nM: 3.4-184 as product\n1.0-50 as H2O2","2010-06-09"]
[]
["#   I: Initial Dose; M: Maintenance Dose, both as product"]

{"sheet":"NaOCl","index":9,"n_rows":109,"n_cols":10,"rows_kept":109,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: Sodium Hypochlorite"]
[]
["Common Name(s)","Trade Name (Manufacturer)*","CAS #","EPA#","PC Code","% NaOCl \nas NaOCl","Slug Dose           (ppm Pdt./ppm Cl2) ","Intermit. Dose                 (ppm Pdt./ppm Cl2) ","Cont. Dose                       (ppm Pdt./ppm Cl2) ","Label\nDate"]
["Sodium Hypochlorite","Sodium Hypochlorite 16% EP\n(K.A. Steel Chemicals Inc.)","7681-52-9","33981-10",14703,16,"I:40-79/5.0-10.0          S:7.9/1.0","I:40-79/5.0-10.0**\nS:7.9/1.0**","I:40-79/5.0-10.0          S:7.9/1.0***","2011-02-22"]
["Sodium Hypochlorite","Sodium Hypochlorite 15.5%\n(Kuehne Chemical Co., Inc.)","7681-52-9","35317-7",14703,15.5,"I:51-102/5.0-10.0\nS:10.7/1.0","I:51-102/5.0-10.0**\nS:10.7/1.0**","I:51-102/5.0-10.0\nS:9.8/1.0***","2011-01-19"]
["Sodium Hypochlorite","Alpha Chlor\n(Alpha Water Systems, Inc.)","7681-52-9","74208-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-05-04"]
["Sodium Hypochlorite","Aqua Guard Bleach\n(Allied Universal Corp.)","7681-52-9","33458-22",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-11-09"]
["Sodium Hypochlorite","Azone 15\n(Hawkins Inc.)","7681-52-9","7870-5",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-08-13"]
["Sodium Hypochlorite","Bacticide\n(Pioneer Americas, LLC)","7681-52-9","37982-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2005-03-14"]
["Sodium Hypochlorite","Bleach Sanitizer\nABC Compounding Co., Inc.)","7681-52-9","3862-183",14703,12.5,"I:77-154/7.5-15.0     S:39-77/3.75-7.5",null,null,"2009-02-12"]
["Sodium Hypochlorite","Bleach Tech 12.5% Solution\n(Bleach Tech LLC)","7681-52-9","75373-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2003-03-31"]
["Sodium Hypochlorite","Buckman's Liquid Shock\n(Buckman\"s Inc.)","7681-52-9","42052-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2012-01-17"]
["Sodium Hypochlorite","Busan 1125C\n(Buckman Laboratories Inc.)","7681-52-9","1148-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-07-28"]
["Sodium Hypochlorite","Cascade S100L\n(Cascade Water Services, Inc.)","7681-52-9","47033-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2003-10-22"]
["Sodium Hypochlorite","ChemCal 1512\n(ChemCal Inc.)","7681-52-9","53431-14",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-02-05"]
["Sodium Hypochlorite","Dixichlor Max\n(DPC Industries, Inc.)","7681-52-9","813-15",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2011-02-28"]
["Sodium Hypochlorite","DYNACHLOR\n(Zee Company Inc.)","7681-52-9","12446-1",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-01-12"]
["Sodium Hypochlorite","Flo-Klor\n(Flo-Kem, Inc.)","7681-52-9","10693-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2008-12-16"]
["Sodium Hypochlorite","Formula 305\n(Garratt-Callahan Co.)","7681-52-9","8540-16",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-03-01"]
["Sodium Hypochlorite","Formula 1582\n(Eastern Technologies, Inc.)","7681-52-9","56485-3",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2002-04-03"]
["Sodium Hypochlorite","Full Chlor\n(Fuller Engineering Inc)","7681-52-9","87309-1",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-05-21"]
["Sodium Hypochlorite","GenChlor 12.5%\n(General Alum New England Corp.)","7681-52-9","80656-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2004-07-15"]
["Sodium Hypochlorite","Generic Bleach 12.5%\n(The Clorox Co.)","7681-52-9","5813-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2004-05-07"]
["Sodium Hypochlorite","Hasachlor\n(Hasa, Inc.)","7681-52-9","10897-26",14703,12.5,"I:47-94/5.0-10.0           S:9.4/1.0","I:47-94/5.0-10.0**           S:9.4/1.0**","I:47-94/5.0-10.0           S:9.4/1.0***","2009-10-30"]
["Sodium Hypochlorite","Hasa Sani-Chlor\n(Hasa, Inc.)","7681-52-9","10897-4",14703,12.5,"I:47-94/5.0-10.0           S:9.4/1.0","I:47-94/5.0-10.0**           S:9.4/1.0**","I:47-94/5.0-10.0           S:9.4/1.0***","2009-10-08"]
["Sodium Hypochlorite","Hypo 150\n(Rowell Chemical Corp.)","7681-52-9","67649-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2008-10-21"]
["Sodium Hypochlorite","HYPOCHLOR\n(Amerochem Corp.)","7681-52-9","65692-1",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2006-02-08"]
["Sodium Hypochlorite","Hypochlorite Solution\n(H. Krevit & Co., Inc.)","7681-52-9","52483-1",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2012-02-06"]
["Sodium Hypochlorite","LA Chemchlor\n(Brenntag Pacific, Inc.)","7681-52-9","66887-4",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2009-05-07"]
["Sodium Hypochlorite","Liquichlor 12.5% Solution\n(Univar USA, Inc.)","7681-52-9","550-198",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2011-08-22"]
["Sodium Hypochlorite","Nalco 7341\n(Nalco Company)","7681-52-9","1706-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2009-11-06"]
["Sodium Hypochlorite","Pure Bright 12.5% Sodium Hypochlorite Solution Bleach (Kik Intl. Inc.)","7681-52-9","70271-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-08-03"]
["Sodium Hypochlorite","PVS Nolwood Sodium Hypochlorite 12.5% Solution (PVS Nolwood Chemicals, Inc.)","7681-52-9","62255-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-04-14"]
["Sodium Hypochlorite","Reg 13\n(Anderson Chemical Co.)","7681-52-9","150-64",14703,12.5,"I:47-84/5.0-10.0           S:7.5/1.0","I:47-84/5.0-10.0**           S:7.5/1.0**","I:47-84/5.0-10.0           S:7.5/1.0***","2010-07-13"]
["Sodium Hypochlorite","Seaboard Liquid Shock\n(Seaboard Industries)","7681-52-9","7152-88",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2007-09-21"]
["Sodium Hypochlorite","Slimicide C-70\n(GE Betz, Inc.)","7681-52-9","3876-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-07-14"]
["Sodium Hypochlorite","Sodium Hypochlorite 12.5%\n(Alexander Chemical Corp.)","7681-52-9","7151-20001",14703,12.5,"I:51-101/5.0-10.0\nS:11.3/1.0","I:51-101/5.0-10.0**\nS:11.3/1.0**","I:51-101/5.0-10.0\nS:9.4/1.0***","2011-05-02"]
["Sodium Hypochlorite","Sodium Hypochlorite (12.5%)\n(Basic Chemical Solutions, LLC)                                 ","7681-52-9","70567-2",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-04-28"]
["Sodium Hypochlorite","12.5% Sodium Hypochlorite\n(Brenntag Pacific, Inc.)","7681-52-9","66887-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2008-10-21"]
["Sodium Hypochlorite","Sodium Hypochlorite\n(FMC Lithium Division)","7681-52-9","7675-13",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2005-09-13"]
["Sodium Hypochlorite","12.5% Sodium Hypochlorite\n(Formosa Plastics Corp.)","7681-52-9","85374-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:3.1/1.0***","2011-05-03"]
["Sodium Hypochlorite","Sodium Hypochlorite 12.5%\n(Hacros Chemicals Inc.)","7681-52-9","148-1288",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2009-12-01"]
["Sodium Hypochlorite","Sodium Hypochlorite 12.5%\n(Hydride Chemical Co.)","7681-52-9","2686-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:14.1/1.0***","2012-05-22"]
["Sodium Hypochlorite","Sodium Hypochlorite\n(SAL Chemical Co., Inc.)","7681-52-9","62833-1",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0",null,null,"2010-08-31"]
["Sodium Hypochlorite","Sodium Hypochlorite-12.5 Bacticide\n(Olin Corporation)","7681-52-9","72315-6",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2011-10-06"]
["Sodium Hypochlorite","Sodium Hypochlorite Sanitizer\n(Chemstation International Inc.)","7681-52-9","65072-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2006-09-26"]
["Sodium Hypochlorite","Sodium Hypochlorite Solution 12.5%\n(Brenntag Mid-South, Inc.)","7681-52-9","6785-4",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2010-09-23"]
["Sodium Hypochlorite","Sodium Hypochlorite Solution\n(George S. Coyne Chemical Co. Inc.)","7681-52-9","41934-2",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0",null,null,"2010-04-14"]
["Sodium Hypochlorite","Sodium Hypochlorite Solution\n(K. A. Steel Chemicals Inc.)","7681-52-9","33981-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2011-06-06"]
["Sodium Hypochlorite","Sodium Hypochlorite Solution\n(Kuehne Chemical Co., Inc.)","7681-52-9","35317-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2011-01-19"]
["Sodium Hypochlorite","Sodium Hypochlorite Solution\n(Warsaw Chemical Co., Inc.)","7681-52-9","2230-20001",14703,12.5,"I:49-98/5.0-10.0   S:10.3/1.0","I:49-98/5.0-10.0**   S:10.3/1.0**","I:49-98/5.0-10.0   S:9.4/1.0***","2006-09-19"]
["Sodium Hypochlorite","BCS Sodium Hypochlorite (11.9%)\n(Basic Chemical Solutions, L.L.C.)","7681-52-9","70567-4",14703,11.9,"I:50-100/5.0-10.0        S:10.2/1.0","I:50-100/5.0-10.0**        S:10.2/1.0**","I:50-100/5.0-10.0        S:11.6/1.0***","2010-08-19"]
["Sodium Hypochlorite","Sodium Hypochlorite 11.5%\n(Kuehne Chemical Co., Inc.)","7681-52-9","35317-5",14703,11.5,"48-96/5.0-10.0     S:10.1/1.0","48-96/5.0-10.0**     S:10.1/1.0**","48-96/5.0-10.0     S:9.2/1.0***","2009-08-05"]
["Sodium Hypochlorite","Sodium Hypochlorite 10.8%\n(Brenntag Canada, Inc.)","7681-52-9","86027-1",14703,10.8,"I:54-109/5.0-10.0\nS:10.9/1.0","I:54-109/5.0-10.0**\nS:10.9/1.0**","I:54-109/5.0-10.0\nS:10.9/1.0***","2009-10-08"]
["Sodium Hypochlorite","Aqua Chlor Chlorinating Solution\n(Chemical Formulators, Inc.)","7681-52-9","70529-20002",14703,10.5,"I:50-100/5.0-10.0       S:10.0/1.0","I:50-100/5.0-10.0**S:10.0/1.0**","I:50-100/5.0-10.0       S:10.0/1.0***","1997-09-17"]
["Sodium Hypochlorite","Aqua Guard Chlorinating Sanitizer\n(Allied Universal Corp.)","7681-52-9","33458-23",14703,10.5,"I:49-98/5.0-10.0   S:10.9/1.0","I:49-98/5.0-10.0**   S:10.9/1.0**","I:49-98/5.0-10.0   S:13.6/1.0***","2011-07-20"]
["Sodium Hypochlorite","Commercial Chlor\n(PoolSure, Inc.)","7681-52-9","82289-1",14703,10.5,"I:49-98/5.0-10.0   S:10.9/1.0","I:49-98/5.0-10.0**   S:10.9/1.0**","I:49-98/5.0-10.0   S:13.6/1.0***","2009-02-13"]
["Sodium Hypochlorite","Sodium Hypochlorite Solution 10.5\n(Kuehne Chemical Co., Inc.)","7681-52-9","35317-4",14703,10.5,"I:47-94/5.0-10.0           S:10.0/1.0","I:47-94/5.0-10.0**           S:10.0/1.0**","I:47-94/5.0-10.0           S:9.1/1.0***","2009-08-05"]
["Sodium Hypochlorite","Sodium Hypochlorite Solution 10.5% By Weight (Brenntag Mid-South, Inc.)","7681-52-9","53257-6",14703,10.5,"I:47-94/5.0-10.0           S:10.0/1.0","I:47-94/5.0-10.0**           S:10.0/1.0**","I:47-94/5.0-10.0           S:9.1/1.0***","2010-07-21"]
["Sodium Hypochlorite","Azone Disinfectant Germicide Sanitizer\n(Hawkins Inc.)","7681-52-9","7870-5",14703,10,"I:49-97/5.0-10.0           S:10.8/1.0","I:49-97/5.0-10.0**           S:10.8/1.0**","I:49-97/5.0-10.0           S:9.0/1.0***","2010-08-11"]
["Sodium Hypochlorite","BCS Sodium Hypochlorite (10%)\n(Basic Chemical Solutions, L.L.C.)","7681-52-9","70567-3",14703,10,"I:49-97/5.0-10.0\nS:10.8/1.0","I:49-97/5.0-10.0**\nS:10.8/1.0**","I:49-97/5.0-10.0\nS:11.3/1.0***","2011-04-18"]
["Sodium Hypochlorite","Biosperse 3001\n(Drew Industrial Div., Ashland Chem.Co.)","7681-52-9","1757-95",14703,10,"I:721-7209/60-600 in RCW using drip pan****                            S:Repeat as needed                                   ","I:11.3/1.0 for 4 hr using drip pan\nS.Repeat to maintain 1.0 as Cl2.",null,"2009-07-16"]
["Sodium Hypochlorite","Busan 1125\n(Buckman Laboratories Inc.)","7681-52-9","1448-20002",14703,10,"I:47-94/5.0-10.0\nS:9.9/1.0","I:47-94/5.0-10.0**\nS:9.9/1.0**","I:47-94/5.0-10.0\nS:9.0/1.0***","2011-02-03"]
["Sodium Hypochlorite","Dixichlor\n(DPC Industries, Inc.)","7681-52-9","813-16",14703,10,"I:61-123/5.0-10.0\nS:11.7/1.0","I:61-123/5.0-10.0**\nS:11.7/1.0**","I:61-123/5.0-10.0\nS:13.5/1.0***","2011-02-28"]
["Sodium Hypochlorite","Hasa Liquid Chlorinating Compound\n(Hasa, Inc.)","7681-52-9","10897-24",14703,10,"I:58-115/5.0-10.0           S:11.7/1.0","I:58-115/5.0-10.0**           S:11.7/1.0**","I:58-115/5.0-10.0           S:11.7/1.0***","2009-10-30"]
["Sodium Hypochlorite","Liquichlor 10% Solution\n(Univar USA Inc.)","7681-52-9","550-197",14703,10,"I:59-117/5.0-10.0          S:12.4/1.0","I:59-117/5.0-10.0**\nS:12.4/1.0**","I:59-117/5.0-10.0\nS:11.3/1.0***","2011-08-22"]
["Sodium Hypochlorite","Pure Birght 10% Sodium Hypochlorite Solution (Kik Intl. Inc.)","7681-52-9","70271-10",14703,10,"I:58-115/5.0-10.0\nS:11.7/1.0","I:58-115/5.0-10.0**\nS:11.7/1.0**","I:58-115/5.0-10.0         S:13.5/1.0***","2010-07-26"]
["Sodium Hypochlorite","PVS Nolwood 10.0% Sodium Hypochlorite Solution\n(PVS Nolwood Chemicals, Inc.)","7681-52-9","62255-20002",14703,10,"I:60-121/5.0-10.0        S:12.6/1.0","I:60-121/5.0-10.0**\nS:12.6/1.0**","I:60-121/5.0-10.0\nS:13.5/1.0***","2010-04-15"]
["Sodium Hypochlorite","Sodium Hypochlorite 10\n(Dycho Co.)","7681-52-9","34750-20002",14703,10,null,null,"I:18.8/2.0\nS:18.8/2.0***","2010-10-28"]
["Sodium Hypochlorite","10% Sodium Hypochlorite\n(Formosa Plastics Corp.)","7681-52-9","85374-20002",14703,10,"I:56-105/5.0-10.0   S:11.7/1.0","I:56-105/5.0-10.0**  S:11.7/1.0**","I:56-105/5.0-10.0   S:9.0/1.0***","2010-05-24"]
["Sodium Hypochlorite","Sodium Hypochlorite 10%\n(Harcros Chemicals, Inc.)","7681-52-9","148-628",14703,10,"I:59-117/5.0-10.0         S:12.4/1.0","I:59-117/5.0-10.0**         S:12.4/1.0**","I:59-117/5.0-10.0         S:11.3/1.0***","2009-12-09"]
["Sodium Hypochlorite","Sodium Hypochlorite\n(Hill Brothers Chemical Co.)","7681-52-9","266-20002",14703,10,"I:54-108/5.0-10.0          S:10.8/1.0","I:54-108/5.0-10.0**         S:10.8/1.0**","I:54-108/5.0-10.0          S:13.5/1.0***","2008-04-10"]
["Sodium Hypochlorite","Sodium Hypochlorite 10\n(Olin Chlor Alkali Products)","7681-52-9","72315-14",14703,10,"I:58-115/5.0-10.0         11.5/1.0","I:58-115/5.0-10.0**         11.5/1.0**","I:58-115/5.0-10.0         11.7/1.0***","2012-05-16"]
["Sodium Hypochlorite","Sodium Hypochlorite Solution 10%\n(K.A. Steel Chemicals, Inc.)","7681-52-9","33981-20002",14703,10,"I:58-115/5.0-10.0         11.5/1.0","I:58-115/5.0-10.0**         11.5/1.0**","I:58-115/5.0-10.0         11.7/1.0***","2009-02-11"]
["Sodium Hypochlorite","Sno Glo Bleach\n(Brenntag Mid-South, Inc.)","7681-52-9","6785-20002",14703,10,"I:60-122/5.0-10.0         S:11.7/1.0","I:60-122/5.0-10.0**        S:11.7/1.0**","I:60-122/5.0-10.0         S:11.7/1.0***","2012-03-15"]
["Sodium Hypochlorite","DIBAC\n(JohnsonDiversey, Inc.)","7681-52-9","875-47",14703,9.1999999999999993,null,null,"I:52-103/5.0-10.0         S:8.9/1.0***","2010-02-19"]
["Sodium Hypochlorite","Liqui-Chlor\n(Petra Chemical Co.)","7681-52-9","62495-3",14703,9.1999999999999993,"I:96-191/7.5-15.0                          S:48-96/3.75-7.5",null,null,"2001-09-07"]
["Sodium Hypochlorite","Liquichlor 9.2% Solution\n(Univar USA Inc.)","7681-52-9","550-20003",14703,9.1999999999999993,null,"I:52-103/5.0-10.0**        S:12.5/1.0**","I:52-103/5.0-10.0         S:17.8/1.0***","2011-08-22"]
["Sodium Hypochlorite","Liquid Chlorinating Product\n(Alpha Chemical Services Inc.)","7681-52-9","10634-20003",14703,9.1999999999999993,"I:52-103/5.0-10.0         S:12.5/1.0",null,"I:52-103/5.0-10.0         S:12.5/1.0***","2009-08-20"]
[null,"L.T. Sanitizer 9.2%\n(Pioneer Americas, L.L.C.)","7681-52-9","37982-20003",14703,9.1999999999999993,"I:62-124/5.0-10.0          S:12.5/1.0","I:62-124/5.0-10.0**          S:12.5/1.0**","I:62-124/5.0-10.0          S:13.4/1.0***","2004-01-08"]
["Sodium Hypochlorite","Sodium Hypochlorite 9\n(Olin Corp.)","7681-52-9","72315-4",14703,9,"I:49-115/5.0-10.0          S:11.5/1.0","I:49-115/5.0-10.0**          S:11.5/1.0**","I:49-115/5.0-10.0          S:11.5/1.0***","2012-05-15"]
["Sodium Hypochlorite","Massosoit A\n(Kik International Inc.)","7681-52-9","70271-26",14703,8,"I:70-140/5.0-10.0          S:14.0/1.0","I:70-140/5.0-10.0**         S:14.0/1.0**","I:70-140/5.0-10.0          S:17.5/1.0***","2010-12-09"]
["Sodium Hypochlorite","San-I-Queen\n(US Chemical Corp.)","7681-52-9","7546-3",14703,6.4,"I:85-171/5.0-10.0         S:17.1/1.0","I:85-171/5.0-10.0**         S:17.1/1.0**","I:85-171/5.0-10.0         S:17.1/1.0***","2010-03-31"]
["Sodium Hypochlorite","Austin A-1 Ultra Disinfecting Bleach\n(James Austin Col.)","7681-52-9","1672-65",14703,6,"I:91-181/5.0-10.0         S: 17.8/1.0","I:91-181/5.0-10.0**         S: 17.8/1.0**","I:91-181/5.0-10.0         S: 17.0.1/1.0***","2011-11-16"]
["Sodium Hypochlorite","Hasa Bleach 6%\n(Hasa, Inc.)","7681-52-9","10897-108",14703,6,"I:94-183/5.0-10.0         S:18.7/1.0","I:94-183/5.0-10.0**         S:18.7/1.0**","I:94-183/5.0-10.0         S:18.7/1.0***","2011-12-15"]
["Sodium Hypochlorite","Huish-Sodium Hypochlorite 6.0%\n(Kik Int. Inc.)","7681-52-9","70271-16",14703,6,"I:91-181/5.0-10.0         S:18.1/1.0","I:91-181/5.0-10.0**         S:18.1/1.0**","I:91-181/5.0-10.0         S:17.8/1.0***","2008-06-24"]
["Sodium Hypochlorite","Pure Bright Germicidal Ultra Bleach\n(Kik Tntl. Inc.)","7681-52-9","70271-13",14703,6,"I:91-181/5.0-10.0          18.7/1.0","I:91-181/5.0-10.0**          18.7/1.0**","I:91-181/5.0-10.0          21/1.0***","2011-07-14"]
["Sodium Hypochlorite","Regular Scent Bleach\n(GS Liquid Technologies, LLC)","7681-52-9","84697-1",14703,6,"I:44-88/5.0-10.0           S:9.3/1.0","I:22-44/5.0-10.0**        S:4.2/1.0**","I:22-44/5.0-10.0           S:8.5/1.0***","2011-02-28"]
["Sodium Hypochlorite","Chem Bleach Household DRP\n(Brenntag Mid-South, Inc.)","7681-52-9","66426-3",14703,5.25,"I:117-234/5.0-10.0                      S:24/1.0","I:117-234/5.0-10.0**        S:2.5/1.0**","I:117-234/5.0-10.0                       S:25/1.0***","2011-01-06"]
["Sodium Hypochlorite","Dixichlor Lite\n(DPC Industries, Inc.)","7681-52-9","813-14",14703,5.25,"I:109-218/5.0-10.0       S:25/1.0","I:109-218/5.0-10.0**       S:25/1.0**","I:109-218/5.0-10.0       S:25/1.0***","2011-02-28"]
["Sodium Hypochlorite","Econo-Clor Sodium Hypochlorite 5.25%\n(Surpass Chemical Co., Inc.)","7681-52-9","9359-2000",14703,5.25,"I:44-87/5.0-10.0                S:9.2/1.0","I:44-87/5.0-10.0**                S:9.2/1.0**","I:44-87/5.0-10.0                S:8.4/1.0***","2011-05-05"]
["Sodium Hypochlorite","Hasa Bleach 5.25%\n(Hasa, Inc.)","7681-52-9","10897-107",14703,5.25,"I:108-215/5.0-10.0        S:21/1.0","I:108-215/5.0-10.0**        S:21/1.0**","I:108-215/5.0-10.0        S:21/1.0***","2010-04-16"]
["Sodium Hypochlorite","Liquichlor 5.25%\n(Univar USA Inc.)","7681-52-9","550-199",14703,5.25,"I:104-208/5.0-10.0         S:22/1.0","I:104-208/5.0-10.0**         S:13/6/1.0**","I:104-208/5.0-10.0         S:20/1.0***","2011-08-22"]
["Sodium Hypochlorite","L.T. Sanitizer 5.25%\n(Pioneer Americas, LLC)","7681-52-9","37982-20004",14703,5.25,"I:103-205/5.0-10.0          S:20.6/1.0","I:103-205/5.0-10.0**          S:20.6/1.0**","I:103-205/5.0-10.0          S:21.0/1.0***","2012-05-15"]
["Sodium Hypochlorite","Pure Bright Disinfection Bleach\n(Kik Intl. Inc.)","7681-52-9","70271-3",14703,5.25,"I:103-205/5.0-10.0        S:21/1.0","I:103-205/5.0-10.0**        S:21/1.0**","I:103-205/5.0-10.0        S:25/1.0***","2010-05-27"]
["Sodium Hypochlorite","PVS Nolwood Sodium\nHypochlorite 5.25% Solution\n(PVS Nolwood Chemicals, Inc.)","7681-52-9","62255-20004",14703,5.25,"I:119-239/5.0-10.0       S:25/1.0","I:119-239/5.0-10.0**       S:25/1.0**","I:119-239/5.0-10.0       S:25/1.0**","2010-04-14"]
["Sodium Hypochlorite","Sodium Hypochlorite\n(Diversey, Inc.)","7681-52-9","875-93",14703,5.25,null,null,"I:105-210/5.0-10.0             S:21/1.0***","2010-03-05"]
["*PAN Pesticides Database-Chemicals"]
["**Apply half (or 1/3, 1/4, or 1/5) of the initial dose when half (or 1/3, 1/4, or 1/5) of the water has been blown down."]
["***Dose: lb Product fed per million lb of blowdown"]

{"sheet":"NaOCL Decay","index":10,"n_rows":96,"n_cols":7,"rows_kept":96,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
["Copied directly from: 05/03/13"]
["Sodium Hypochlorite degradation with time"]
[]
["http://www.miox.com/treatment-challenges/DegBleachCalc.aspx"]
[]
[]
["Predicting the Rate of Commercial Bleach Degradation"]
["Bleach 20011, a software program that accurately (within 10% over a broad range of initial FAC "]
["concentrations and temperatures) predicts the rate of commercial bleach degradation to chlorate is "]
["available from the Water Research Foundation. This program was compiled after detailed laboratory "]
["studies were used to confirm the model developed by Gordon et al.2 For those interested in obtaining "]
["detailed information regarding bleach degradation rates and the factors that impact bleach degradation, "]
["this program should be acquired."]
[]
["Due to numerous customer inquiries, MIOX developed a Bleach Degradation Calculator (Calculator). The "]
["calculator at this website is an approximation of the Bleach 2001 model and is offered to customers as a "]
["tool for approximating commercial bleach degradation rates in the pH 11-14 range. It should NOT be "]
["used to predict degradation rates for on-site generated hypochlorite solutions due to their lower initial "]
["FAC concentration and lower pH. If OSG solutions are used within 48 hours, the rates of degradation are "]
["typically not of concern."]
[]
["The Calculator predictions and the Bleach 2001 Model predictions are in close agreement at initial FAC "]
["concentrations ≥6.5 Trade % and storage temperatures ≥59° F (15° C). It is important to note that the "]
["Calculator underestimates the rate of FAC degradation at both lower initial FAC concentrations and lower "]
["storage temperatures compared to Bleach 2001."]
["NOTE:  CALCULATOR AT THE ACTUAL WEBSITE WORKS FOR CALCULATIONS!!!"]
["This one is not fuly functional!",null,null,"Degradation of Bleach Calculator"]
[]
["Days of Storage:",null,null,null,"% Concentration (Predicted)","Days","% Loss in Concentration"]
["% Concentration:",null,null,null,0.1173,7,2.2499999999999999E-2]
["Temperature:",null,null,null,0.1143,15,4.7699999999999999E-2]
[{"$nulls":4},0.10879999999999999,30,9.3100000000000002E-2]
[{"$nulls":4},9.8699999999999996E-2,60,0.1774]
[]
[]
[]
["Days Storage:","% Concentration (Predicted)"]
["0 ",0.12]
["1 ",0.1196]
["2 ",0.1192]
["3 ",0.1188]
["4 ",0.11840000000000001]
["5 ",0.1181]
["6 ",0.1177]
["7 ",0.1173]
["8 ",0.1169]
["9 ",0.11650000000000001]
["10 ",0.1162]
["11 ",0.1158]
["12 ",0.1154]
["13 ",0.115]
["14 ",0.1147]
["15 ",0.1143]
["16 ",0.1139]
["17 ",0.1135]
["18 ",0.1132]
["19 ",0.1128]
["20 ",0.1124]
["21 ",0.11210000000000001]
["22 ",0.11169999999999999]
["23 ",0.1113]
["24 ",0.111]
["25 ",0.1106]
["26 ",0.1103]
["27 ",0.1099]
["28 ",0.1095]
["29 ",0.10920000000000001]
["30 ",0.10879999999999999]
[]
[]
[]
[]
["Notes to Calculator:"]
["MIOX Corporation DOES NOT offer this Calculator as a process guarantee in design and construct of your application."]
["MIOX Corporation only offers this Calculator as a method to approximate bulk bleach degradation of the FAC concentration only over practical "]
["ranges of storage temperature and initial FAC concentrations. The Calculator is not accurate for predicting the degradation rate of MIOX’s "]
["onsite generation products."]
["FAC degradation of bulk bleaches under conditions outside the stated applicability ranges of the Calculator (initial FAC concentrations ≥6.5 Trade % "]
["and storage temperatures ≥59° F (15° C)) and evaluation of the formation of chlorate in the bulk bleaches should be completed using the "]
["Bleach 2001 program."]
[]
[]
["1Adam, Luke, Gilbert Gordon, and Don Pierce. 2001. Bleach 2001. Miami University, Oxford, Ohio. Copyright (c) 2001 AwwaRF and AWWA. Available from the Water Research Foundation."]
["2Gordon, G., L.C. Adam, B.P. Bubnis, C. Kuo, R.S. Cushing, and R.H. Sakaji, 1997, \"Predicting Liquid Bleach Decomposition\", Journal of the American Water Works Association, 89(4):142-149.:"]
[]
["Reference added by AWT Cooling Water Technical Subcommittee, for Hypochloride Degdation:"]
["Water Quality Research Journal, Canada, 1995 Volume 30, No. 2, 339-361."]

{"sheet":"NaOCl-SG","index":11,"n_rows":34,"n_cols":5,"rows_kept":34,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[]
[null,"TABLE 1: Properties of Sodium Hypochlorite Solutions"]
[]
[null,"% NaOCl","% as Cl2","S.G. (g/mL)","Density (lb/gal)"]
[null,5.25,5,1.075,8.9700000000000006]
[null,6,5.72,1.087,9.07]
[null,6.4,6.1,1.0940000000000001,9.1199999999999992]
[null,8,7.62,1.1200000000000001,9.34]
[null,8.34,7.94,1.125,9.3800000000000008]
[null,9,8.57,1.1359999999999999,9.4700000000000006]
[null,9.1999999999999993,8.77,1.1399999999999999,9.51]
[null,10,9.5299999999999994,1.1539999999999999,9.6199999999999992]
[null,10.5,10,1.163,9.6999999999999993]
[null,10.8,10.29,1.1679999999999999,9.74]
[null,11.5,10.95,1.181,9.85]
[null,12,11.43,1.1910000000000001,9.93]
[null,12.5,11.91,1.2,10.01]
[null,15.5,14.76,1.25,10.43]
[null,16,15.24,1.2709999999999999,10.6]
[]
[]
[null,"Note: The specific gravity information was listed in or interpolated from"]
[null,"Table 2 of the OxyChem Sodium Hypochlorite Handbook, Occidental Corp., 2000."]
[null,"Since most labels gave doses in ounces per 10,000 gal or per 1,000 gal,"]
[null,"the specific gravity values were used to convert application rates to ppm product."]

{"sheet":"NaOCl-Stab","index":12,"n_rows":16,"n_cols":8,"rows_kept":16,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: Stabilized Sodium Hypochlorite"]
[]
["Common Name(s)","Trade Name (Manufacturer)*","CAS #","EPA#","PC Code","% NaOCl","Slug Dose           (ppm Pdt./Total Cl2) ","Label\nDate"]
["Sodium Hypochlorite","Acti-Plus 2818 Stabilized Sodium Hypochlorite (Nalco Company)","7681-52-9","1706-171",14703,"8.34\n7.9% Av. Cl2","22.5-45/2.0-4.0          Test and dose until target Total Cl2 is met.","2010-01-07"]
[]
[]
["*PAN Pesticides Database-Chemicals"]

{"sheet":" NaBr","index":13,"n_rows":44,"n_cols":12,"rows_kept":44,"cut":false,"hidden":false,"merged":[[10,1,10,9]]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: = Sodium Bromide (NaBr)"]
[null,"Note:  This product is not biocidal by itself.  It requires activation by an oxidizer such as chlorine gas or sodium hypochlorite (bleach)."]
["Common\nName(s)","Trade Name (Manufacturer)*","CAS #","EPA#","PC Code","PMRA # (Canada)","% NaBr\nas NaBr**","% Av. Br2","Cooling Water Dose (ppm)#","Additional dosing information","Target halogen\nresidual (ppm) ","Label\nDate"]
["Sodium Bromide","HyBrom 99\n(ICL-IP America, Inc.)","7647-15-6","8622-57",13907,null,99,null,null,"0.5 to 2.0 moles NaBr/mole of Oxidant.\n0.3-1.3 lb Cl2 gas or 0.3-1.3 gal NaOCl\n(12.5% as Cl2), or 0.4-1.4 lb Trichlor,\nor 0.5-2.0 lb Dichlor, or 0.5-2.0 lb\nDichlor Dihydrate per lb product","I: Active residual Br2 of\n0.5-5.0 ppm measured\n5 minutes after treatment\nM: Same","2004-05-11"]
["Sodium Bromide","PCT 3023 Microorganism\nControl Chemical\n(ProchemTech Intl., Inc.)","7647-15-6","58616-5",13907,null,46.8,72.7,"Dosing 2.7 ppm (w/w) Product yields about\n1 ppm total Br2.  This product is designed to be used in conjunction with an electrolysis\nunit which converts Br- into active Br2.",null,"Total Br2: 0.5-5 ppm","2005-06-20"]
["Sodium Bromide","BromiCide 4600\n(BWA Water Additives LLC)","7647-15-6","83451-19",13907,null,46,null,"I:  0.3-30 ppm (w/w) Product +\n0.9-5 ppm (w/w) Cl2 gas or 8.3-41 ppm\n(w/w) 12.5% NaOCl\nM: 0.1 -30 ppm (w/w) Product +\n0.4-5 ppm (w/w) Cl2 gas or 3.5 -41 ppm\n(w/w) 12.5% NaOCl ","0.125 to 2.0 moles NaBr/mole of Oxidant.\n2-32 lb Cl2 gas or 1.6-26 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2010-07-08"]
["Sodium Bromide","NABR46-E\n(Bio-Lab Inc.)","7647-15-6","5185-450",13907,null,46,null,"I:  0.3-30 ppm (w/w) Product +\n0.9-5 ppm (w/w) Cl2 gas or 8.3-41 ppm\n(w/w) 12.5% NaOCl\nM: 0.1 -30 ppm (w/w) Product + \n0.4-5 ppm (w/w) Cl2 gas or 3.5 -41 ppm (w/w) 12.5% NaOCl","0.125 to 2.0 moles NaBr/mole of Oxidant.\n2-32 lb Cl2 gas or 1.6-26 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2009-01-06"]
["Sodium Bromide","BioRid 46i\n(Tetra Technologies, Inc.)","7647-15-6","2214-12",13907,null,45.3,35,null,"0.5-2.0 moles NaBr/moles Oxidant.\n1.8-7.6 lb Cl2 gas or 1.5-6.2 gal (15-62 lb)\nNaOCl (12.5%) per gal product","I: Residual Br2: 0.5-2.0 ppm\nM: Residual Br2: 0.5-1.0 ppm","2003-08-07"]
["Sodium Bromide","SANIBROM 45 Biocide (Albemarle)","7647-15-6","3377-29",13907,null,45,null,null,"0.5-2.0 moles NaBr/mole Oxidant.\n1.8-7.6 lb Cl2 gas or 1.5-6.2 gal (15-62 lb)\nNaOCl (12.5%) per gal product (~12.4 lb)","I: Residual Br2: 0.5-2 ppm\nM: Residual Br2: 0.5-1 ppm ","2011-07-08"]
["Sodium Bromide","Sodium Bromide 45%\n(ICL-IP America, Inc.)","7647-15-6","8622-66",13907,null,45,null,null,"0.5 to 2.0 moles NaBr/mole of Oxidant.\n1.5-6.0 lb Cl2 gas or 1.3-5.2 gal NaOCl\n(12.5% as Cl2), or 1.7-6.7 lb Trichlor, or\n2.4-9.5 lb Dichlor, or 2.7-10.7 lb\nDichlor Dihydrate per gal product","I: Active residual Br2 of\n0.5-5.0 ppm measured\n5 minutes after treatment\nM: Same","2004-05-11"]
["Sodium Bromide","BioRid 43i\n(Tetra Technologies, Inc.)","7647-15-6","2214-15",13907,null,43,33,null,"0.5-2.0 moles NaBr/moles Oxidant.\n1.8-7.6 lb Cl2 gas or 1.5-6.2 gal (15-62 lb)\nNaOCl (12.5%) per gal product","I: Residual Br2: 0.5-2.0 ppm\nM: Residual Br2: 0.5-1.0 ppm","2003-08-07"]
["Sodium Bromide","BromiCide 4300\n(BWA Water Additives LLC)","7647-15-6","83451-18",13907,null,43,null,"I:  0.4-32 ppm (w/w) Product +\n0.9-5 ppm (w/w) Cl2 gas or 8.3-41 ppm\n(w/w) 12.5% NaOCl\nM: 0.2 -32 ppm (w/w) Product +\n0.4-5.2 ppm (w/w) Cl2 gas or 3.5 -41 ppm (w/w) 12.5% NaOCl ","0.125 to 2.0 moles NaBr/mole of Oxidant.\n1.8-29.0 lb Cl2 gas or 1.4-23.2 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2010-07-08"]
["Sodium Bromide","NABR43-E\n(Bio-Lab Inc.)","7647-15-6","5185-467",13907,null,43,null,"I:  0.4-32 ppm (w/w) Product + \n0.9-5 ppm (w/w) Cl2 gas or 8.3-41 ppm\n(w/w) 12.5% NaOCl\nM: 0.2 -32 ppm (w/w) Product +\n0.4-5.2 ppm (w/w) Cl2 gas or 3.5 -1 ppm (w/w) 12.5% NaOCl","0.125 to 2.0 moles NaBr/mole of Oxidant.\n1.8-29.0 lb Cl2 gas or 1.4-23.2 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2008-10-28"]
["Sodium Bromide","SODIUM BROMIDE 43%\n(ICL-IP America, Inc.)","7647-15-6","8622-67",13907,null,43,null,null,"0.5-2.0 moles NaBr/mole of Oxidant.\n1.5-6.0 lb Cl2 gas or 1.3-5.2 gal NaOCl\n(12.5% as Cl2), or 1.7-6.7 lb Trichlor, or\n2.4-9.5 lb Dichlor, or 2.7-10.7 lb\nDichlor Dihydrate per gal product","I: Active residual Br2 of\n0.5-5.0 ppm measured\n5 minutes after treatment\nM: Same","2004-05-11"]
["Sodium Bromide","BIoRid 40i\n(Tetra Technologies, Inc.)","7647-15-6","2214-13",13907,null,40,31,null,"0.5-2.0 moles NaBr/moles Oxidant.\n1.8-7.6 lb Cl2 gas or 1.5-6.2 gal (15-62 lb)\nNaOCl (12.5%) per gal product","I: Residual Br2: 0.5-2.0 ppm\nM: Residual Br2: 0.5-1.0 ppm","2003-08-07"]
["Sodium Bromide","BromiCide 4000\n(BWA Water Additives LLC)","7647-15-6","83451-17",13907,null,40,null,"I:  0.4-34 ppm (w/w) Product + \n0.9-4.7 ppm (w/w) Cl2 gas or 8.3-38 ppm (w/w) 12.5% NaOCl\nM: 0.2 -34 ppm (w/w) Product +\n0.4-4.7 ppm (w/w) Cl2 gas or 3.5 -38 ppm (w/w) 12.5% NaOCl ","0.125 to 2.0 moles NaBr/mole of Oxidant.\n1.6-26.5 lb Cl2 gas or 1.3-21.2 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2011-02-08"]
["Sodium Bromide","DREWBROM PRECURSOR      (Hercules Incorporated/\nAshland Chemical Co.)","7647-15-6","74655-29\n1757-109",13907,23624,40,null,null,"0.5-2.0 moles NaBr/mole Oxidant.\n1.5-6.0 lb Cl2 gas or 1.3-5.2 gal\n(13-52 lb) NaOCl (12.5%) per gal product",null,"2009-07-16"]
["Sodium Bromide","H-940 MICROBIOCIDE\n(Nalco)","7647-15-6","1706-217",13907,null,40,null,"I:  0.4-34 ppm (w/w) Product +\n0.9-4.7 ppm (w/w) Cl2 gas or 8.3-38 ppm (w/w) 12.5% NaOCl\nM: 0.2 -34 ppm (w/w) Product +\n0.4-4.7 ppm (w/w) Cl2 gas or 3.5 -38 ppm (w/w) 12.5% NaOCl","0.125 to 2.0 moles NaBr/mole of Oxidant.\n1.6-26.5 lb Cl2 gas or 1.3-21.2 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2003-11-04"]
["Sodium Bromide","NABR40-E                                 (Bio-Lab Inc.)","7647-15-6","5185-451",13907,null,40,null,"I:  0.4-34 ppm (w/w) Product +\n0.9-4.7 ppm (w/w) Cl2 gas or 8.3-38 ppm (w/w) 12.5% NaOCl\nM: 0.2 -34 ppm (w/w) Product +\n 0.4-4.7 ppm (w/w) Cl2 gas or 3.5 -38 ppm (w/w) 12.5% NaOCl","0.125 to 2.0 mole NaBr/mole of Oxidant.\n1.6-26.5 lb Cl2 gas or 1.3-21.2 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2009-01-06"]
["Sodium Bromide","SANIBROM 40 Biocide (Albemarle)","7647-15-6","3377-25",13907,null,40,null,null,"0.5-2.0 moles NaBr/mole Oxidant.\n1.5-6.0 lb Cl2 gas or 1.3-5.2 gal (13-52 lb)\nNaOCl (12.5%) per gal product (~11.8 lb)","I: Residual Br2: 0.5-1.0 ppm\nM: Residual  Br2: 0.5-1.0 ppm\nBiofilm: Res. Br2: 1.0-3.0 ppm ","2009-11-13"]
["Sodium Bromide","SPECTRUS OX109\n(GE Betz, Inc.)","7647-15-6","3876-158",13907,null,40,null,"I:  0.4-34 ppm (w/w) Product +\n0.9-4.7 ppm (w/w) Cl2 gas or 8.3-38 ppm\n(w/w) 12.5% NaOCl\nM: 0.2 -34 ppm (w/w) Product +\n0.4-4.7 ppm (w/w) Cl2 gas or 3.5 -38 ppm (w/w) 12.5% NaOCl","0.125 to 2.0 moles NaBr/mole of Oxidant.\n1.6-26.5 lb Cl2 gas or 1.3-21.2 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2002-02-06"]
["Sodium Bromide","SPECTRUS OX1201\n(GE Betz, Inc.)","7647-15-6","3876-159",13907,21318,40,null,"I:  0.4-34 ppm (w/w) Product +\n0.9-4.7 ppm (w/w) Cl2 gas or 8.3-38 ppm\n(w/w) 12.5% NaOCl\nM: 0.2 -34 ppm (w/w) Product +\n0.4-4.7 ppm (w/w) Cl2 gas or 3.5 -38 ppm (w/w) 12.5% NaOCl","0.125 to 2.0 moles NaBr/mole of Oxidant.\n1.6-26.5 lb Cl2 gas or 1.3-21.2 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2010-04-16"]
["Sodium Bromide","BioRid 38i\n(Tetra Technologies, Inc.)","7647-15-6","2214-14",13907,null,38,29,null,"0.5-2.0 moles NaBr/moles Oxidant.\n1.8-7.6 lb Cl2 gas or 1.5-6.2 gal (15-62 lb)\nNaOCl (12.5%) per gal product","I: Residual Br2: 0.5-2.0 ppm\nM: Residual Br2: 0.5-1.0 ppm","2003-08-07"]
["Sodium Bromide","NABR38-E                            (Bio-Lab Inc)","7647-15-6","5185-466",13907,null,38,null,"I:  0.4-36 ppm (w/w) Product +\n0.9-4.7 ppm (w/w) Cl2 gas or 7-38 ppm\n(w/w) 12.5% NaOCl\nM: 0.2 -36 ppm (w/w) Product +\n0.4-4.7 ppm (w/w) Cl2 gas or 3.5 -38 ppm (w/w) 12.5% NaOCl","0.125 to 2.0 moles NaBr/mole of Oxidant.\n1.5-24.5 lb Cl2 gas or 1.2-19.6 gal NaOCl\n(12.5% as Cl2) per gal product",null,"2009-01-06"]
["Sodium Bromide","NALCO V04S0 Chlorine Enhancer and Extender          (Nalco)","7647-15-6","1706-235",13907,null,30,null," ","Activate with Cl2 at 1.0:0.1 to 1.0:1.0 Cl2:Br-.\n0.48-4.8 lb product per lb Cl2 gas or\n0.61-6.1 lb (0.054-0.54 gal) product per gal NaOCl (12.5% as Cl2). OR Maintain\n1-100 ppm of product in system.","Oxidant residual (as Cl2):\n0.1-10.0 ppm","2010-02-19"]
["Sodium Bromide","PCT 3024 Microorganism\nControl Chemical                  (ProchemTech Intl., Inc.)","7647-15-6","58616-6",13907,null,14.9,34.799999999999997,"Dosing 13.1 ppm (w/w) Product yields about 1 ppm total Br2.  This product is designed to be used in conjunction with an electrolysis unit which converts Br- into active Br2.",null,"Total Br2: 0.5-5 ppm","2007-10-18"]
[{"$nulls":5},"Specific gravity values used in the calculations"]
["*NPIRS Database",{"$nulls":4},"Water",null,null,"8.345 lb/gal"]
["** % by weight per product label",{"$nulls":4},"12.5% Sodium hypochlorite",null,null,"10 lb/gal"]
["#   I: Initial Dose; M: Maintenance Dose, both as product",{"$nulls":4},"42.8% NaBr solution",null,null,"12.2 lb/gal"]
[{"$nulls":5},"46% NaBr",null,null,"12.6 lb/gal"]
["Notes:"]
["Trichlor = trichloro-s-triazinetrione (CAS No. 87-90-1), also called trichloroisocyanuric acid"]
["Dichlor = sodium dichloro-s-triazinetrione (CAS No. 2893-78-9), also called sodium dichloroisocyanurate"]
["Dichlor dihydrate = sodium dichloro-s-triazinetrione dihydrate (CAS No. 51580-86-0), also called sodium dichloroisocyanurate dihydrate"]

{"sheet":"NH4Br","index":14,"n_rows":19,"n_cols":11,"rows_kept":19,"cut":false,"hidden":false,"merged":[[10,1,10,7]]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: = Ammonium Bromide (NH4Br)"]
[null,"Note:  This product is not biocidal by itself.  It requires activation by an oxidizer such as chlorine gas or sodium hypochlorite (bleach)."]
["Common Name(s)","Trade Name                  (Manufacturer)*","CAS #*","EPA#","PC Code","% NH4Br**","% Av Br2","Cooling Water                         Dose (ppm)#","Additional dosing information","Target halogen residual, ppm","Label\nDate"]
["Ammonium Bromide","FUZZICIDE-COMP\n(ICL-IP America, Inc.)","12124-97-9","8622-58",352,99,null,"Typical recommended dosage\nmay be achieved by mixing\n1.5 lbs Cl2 gas or 1.3 gal NaOCl\nwith each aqueous solution\ncontaining 2.2 lb FUZZICIDE in\nthe FUZZICIDE feeder","This product is to be used\nonly in conjunction with:\n1) an oxidant such as NaOCl\n(12.5%) or Cl2 gas (99.9%)\nto produce FUZZICIDE biocide;\nand 2) the FUZZICIDE feeder/delivery system.","I:  0.3-5.0 ppm as total chlorine; M:  same","2010-06-11"]
["Ammonium Bromide","FUZZICIDE-SP\n(ICL-IP America, Inc.)","12124-97-9","8622-76",352,99,null,"Typical recommended dosage\nmay be achieved by mixing\n1.5 lbs Cl2 gas or 1.3 gal NaOCl\nwith each aqueous solution\ncontaining 2.2 lb FUZZICIDE in\nthe FUZZICIDE feeder","This product is to be used\nonly in conjunction with:\n1) an oxidant such as NaOCl\n(12.5%) or Cl2 gas (99.9%)\nto produce FUZZICIDE biocide;\nand 2) the FUZZICIDE feeder/delivery system.","I:  0.3-5.0 ppm as total chlorine; M:  same","2010-06-11"]
["Ammonium Bromide","FUZZICIDE-SOLUTION\n(ICL-IP America, Inc.)","12124-97-9","8622-64",352,35,null,"The recommended dosage is\ntypically achieved by mixing\n0.54 gal NaOCl (12.5%) with\n0.22 gal FUZZICIDE SOLUTION\nin the reactor","This product is to be used\nonly in conjunction with:\n1) an oxidant such as NaOCl\n(12.5%) or Cl2 gas (99.9%)\nto produce FUZZICIDE biocide;\nand 2) the FUZZICIDE feeder/delivery system.","I:  0.3-5.0 ppm as total chlorine; M:  same","2010-08-26"]
[]
["*NPIRS Database"]
["** % by weight per product label"]
["#   I: Initial Dose; M: Maintenance Dose, both as product"]

{"sheet":"Peracetic Acid","index":15,"n_rows":31,"n_cols":10,"rows_kept":31,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: Peroxyacetic Acid"]
[]
["Common Name(s)","Trade Name (Manufacturer)*","CAS #","EPA#","PC Code","Composition","Slug Dose           (ppm Product/          ppm PAA)**","Intermit. Dose                 (ppm Product/        ppm  PAA)**","Cont. Dose                       (ppm Product/                 ppm PAA)**","Label\nDate"]
["Peroxyacetic Acid","Surpass 100***                                            (EcoLabs, Inc.)","PAA: 79-21-0       H2O2: 7722-84-1","1677-189","H2O2: 595\nPAA: 63201","27.0% H2O2 /4.50% PAA","I:150-600                       S:75-300","I:150-600                       S:75-300","I:150-600                     S:60-240","2012-05-10"]
["Peroxyacetic Acid","Peraclean 5                                                 (Evonik Degussa)","PAA: 79-21-0       H2O2: 7722-84-1","54289-3","H2O2: 595\nPAA: 63201","26.5% H2O2 /4.90% PAA",null,"36-180/1.8-8.8","36-180/1.8-8.8","2011-07-14"]
["Peroxyacetic Acid","Perasan A                                                  (Envirotech)","PAA: 79-21-0       H2O2: 7722-84-1","63838-1","H2O2: 595\nPAA: 63201","26.5% H2O2 /5.60% PAA","206/10.3","36-180/2.0-9.0","36-180/2.0-9.0","2012-06-19"]
["Peroxyacetic Acid","Proxitane 15:23                                             (Solvay)","PAA: 79-21-0       H2O2: 7722-84-1","68660-12","H2O2: 595\nPAA: 63201","23.0% H2O2 /15.0% PAA","6.6-60/1.0-9.0","6.6-60/1.0-9.0","6.6-60/1.0-9.0","2010-03-30"]
["Peroxyacetic Acid","Sanidate 5.0                                                   (BioSafe Systems)","PAA: 79-21-0       H2O2: 7722-84-1","70299-19","H2O2: 595\nPAA: 63201","23.0% H2O2 /5.00% PAA","25-176/2.0-9.0","25-176/2.0-9.0","25-176/2.0-9.0","2012-07-06"]
["Peroxyacetic Acid","Sanidate 5.0 Sanitizer                                     (BioSafe Systems)**","PAA: 79-21-0       H2O2: 7722-84-1","70299-11","H2O2: 595\nPAA: 63201","23.0% H2O2 /5.30% PAA","25-176/2.0-9.0","25-176/2.0-9.0","25-176/2.0-9.0","2010-01-23"]
["Peroxyacetic Acid","Vigorox 15/23 Antimicrobial Agent              (FMC)","PAA: 79-21-0       H2O2: 7722-84-1","65402-8","H2O2: 595\nPAA: 63201","23.0% H2O2 /15.0% PAA",null,"I:96-144                        S:120","I:96-144                        S:≤120                            120 ppm = 17 PAA + 26 H2O2","2011-03-11"]
["Peroxyacetic Acid","BioSide HS 15%                                          (Envirotech)","PAA: 79-21-0       H2O2: 7722-84-1","63838-2","H2O2: 595\nPAA: 63201","22.0% H2O2 /15.0% PAA","44-177/7.0-27","44-89/7.0-14.0","13.3-67/2.0-10.0","2010-11-29"]
["Peroxyacetic Acid","Peraclean 15% (Peroxyacetic Acid Solution)   (Evonik Degussa)","PAA: 79-21-0       H2O2: 7722-84-1","54289-4","H2O2: 595\nPAA: 63201","22.0% H2O2 /15.0% PAA",null,"12.0-60 /1.8-9.0","12.0-60 /1.8-9.0","2010-04-07"]
["Peroxyacetic Acid","Vigorox Antimicrobial Agent                           (FMC)","PAA: 79-21-0       H2O2: 7722-84-1","65402-2","H2O2: 595\nPAA: 63201","21.7% H2O2 /5.10% PAA",null,"I:120-180                     S:120","I:120-180                             S:<180                                180 = 10 PAA + 40 H2O2","2010-05-15"]
["Peroxyacetic Acid","Proxitane WW-12                                           (Solvay)","PAA: 79-21-0       H2O2: 7722-84-1","68660-1","H2O2: 595\nPAA: 63201","18.5% H2O2 /12.0% PAA","10-70/1.0-9.0","10-70/1.0-9.0","10-70/1.0-9.0","2011-04-17"]
["Peroxyacetic Acid","Sanidate 12.0                                                (BioSafe Systems)","PAA: 79-21-0       H2O2: 7722-84-1","70299-18","H2O2: 595\nPAA: 63201","18.5% H2O2 /12.0% PAA","10-70/1.0-9.0","10-70/1.0-9.0","10-70/1.0-9.0","2011-03-14"]
["Peroxyacetic Acid","Sanidate 12.0 Microbiocide                                             (BioSafe Systems)","PAA: 79-21-0       H2O2: 7722-84-1","70299-8","H2O2: 595\nPAA: 63201","18.5% H2O2 /12.0% PAA","10-70/1.0-9.0","10-70/1.0-9.0","10-70/1.0-9.0","2012-03-16"]
["Peroxyacetic Acid","Vigorox 15/10 Antimicrobial Agent                 (FMC)","PAA: 79-21-0       H2O2: 7722-84-1","65402-9","H2O2: 595\nPAA: 63201","10.0% H2O2 /15.0% PAA",null,"I:96-144                        S:120","I:96-144                        S:≤120                            120 ppm = 17 PAA + 12 H2O2","2011-06-07"]
["Peroxyacetic Acid","Vigorox SP-15                                               (FMC)","PAA: 79-21-0       H2O2: 7722-84-1","65402-3","H2O2: 595\nPAA: 63201","10.0% H2O2 /15.0% PAA",null,"I:96-144                        S:120","I:96-144                        S:≤120                            120 ppm = 17 PAA + 12 H2O2","2011-06-07"]
["Peroxyacetic Acid","GreenClean 6% Liquid                                 (BioSafe Systems)","PAA: 79-21-0       H2O2: 7722-84-1","70299-16","H2O2: 595\nPAA: 63201","5.34% H2O2 /1.36% PAA","95-667/1.0-9.0","95-667/1.0-9.0","95-667/1.0-9.0","2012-06-12"]
[]
["*PAN Pesticides Database-Chemicals"]
["**I: Initial: S: Subsequent"]

{"sheet":"Stabilized Liquid Halogens","index":16,"n_rows":27,"n_cols":13,"rows_kept":27,"cut":false,"hidden":false,"merged":[]}
["DISCLAIMER: This document is designed to provide information regarding the subject matter presented.  "]
["It is produced with the understanding that neither AWT nor the contributors are rendering legal, medical, engineering, or other professional services."]
["Neither AWT nor the contributors shall be liable for damages, in any event, for incidental or consequential damages caused, or alleged to be caused,"]
["directly or indirectly, by the use of any information disclosed in this document, including the use of any recommendations, methods, products, services, instructions, or ideas."]
["This is considered a “living documents” and as such will be updated as members contribute new information."]
["Current as of 7/16/13"]
[]
[]
[]
[null,"Biocide Selection Table: = Stabilized Liquid Halogen"]
[]
["Common Name(s)","Trade Name (Manufacturer)*","CAS #**","EPA#","PC Code","PMRA # (Canada)","Composition***","% Total\nAv\nBr2","% Av\nCl2","% Total as\nCl2","Cooling Water                         Dose (ppm)#","Target halogen residual, ppm","Label\nDate"]
["Stabilized liquid bromine","BromMax               (Enviro Tech Corp.)","7647-15-6\n7681-52-9","63838-3","13907\n14703",null,"Sodium hypochlorite, 10.70%; Sodium bromide, 14.77%",23,null,10.199999999999999,"~ 15.6 ppm product by vol results in theoretical of\n~ 5.1 ppm total Br2","Intermittent:\nI: 1-15 ppm total Br2\nContinuous:\n1-3 ppm total Br2","2008-10-23"]
["Stabilized liquid bromine","MAXXIS Biocide (Albemarle)","134509-56-1\n13637-90-6\n1192047-23-6\n1192047-27-0","3377-79",28964,null,"Sodium Bromosulfamate, Sodium Chlorosulfamate, Potassium Bromosulfamate, Potassium Chlorosulfamate, 25.0%",21,null,9,"~ 19.5 ppm product by vol results in theoretical of\n~ 6.2 ppm total Br2 in a demand-free water","I:  4-10 ppm total Br2\nM: Same","2010-06-02"]
["Stabilized liquid bromine","STABROM Plus Biocide (Albemarle)","134509-56-1\n13637-90-6","3377-78",28961,null,"Sodium Bromosulfamate and Sodium Chlorosulfamate, 22%",18,null,8,"~ 23.4 ppm product by vol results in theoretical of\n~ 6.2 ppm total Br2 in a demand-free water","I:  4-10 ppm total Br2\nM: Same","2010-06-02"]
["Stabilized liquid bromine","Albemarle S909 Biocide (Albemarle)","134509-56-1\n13637-90-6","3377-55",28961,null,"Sodium Bromosulfamate and Sodium Chlorosulfamate, 18%",15,null,7,"~ 31.2 ppm product by vol results in theoretical of\n~ 6.4 ppm total Br2 in a demand-free water","I:  4-10 ppm total Br2\nM: Same","2012-01-05"]
["Stabilized liquid bromine","STABILIZED BROMINE SOLUTION                        (ICL-IP America, Inc.)","134509-56-1","8622-81",28960,null,"Sodium Bromosulfamate, 17.0%",null,null,null,"~ 31.2 ppm product by vol results in theoretical of\n~ 6.4 ppm as total Br2 in a demand-free water","I:  4-10 ppm total Br2\nM: Same","2010-04-13"]
["Stabilized liquid bromine","BromMax 7.1              (Enviro Tech Corp.)","7647-15-6\n681-52-9","63838-5",null,29408,"Sodium Hypochlorite, 7.45%; SodiumBbromide, 10.28%",16,null,7,"~ 15.6 ppm product by vol results in theoretical of\n~ 3.4 ppm total Br2","1-15 ppm total Br2","2008-10-23"]
["Stabilized liquid bromine","PCT 3026\n(ProChemTech)","7647-15-6\n681-52-9","58616-1","13907\n14703",null,"Sodium Hypochlorite, 6.36%; Sodium Bromide, 9.14%",14,null,6.4,"~ 15.6 ppm product by vol results in theoretical of\n~ 2.2 ppm total Br2 ","4.5-9 ppm total Br2","2009-10-30"]
["Stabilized liquid bromine","STABREX ST-70  (Nalco)",null,"1706-179","13907\n14703",25478,"Sodium Hypochlorite, 6.36%; Sodium Bromide, 9.23%",14,null,6.4,"~ 15.6 ppm product by vol results in theoretical of\n~ 2.2 ppm total Br2 ","4.5-9 ppm total Br2","2010-01-07"]
[]
["Stabilized liquid chlorine","Justeq07             (Justeq, LLC)","7647-15-6\n7681-52-9","84024-1","13907\n14703",null,"Sodium Hypochlorite, 7.0%; Sodium Bromide, 1.5%",2.2999999999999998,6.7,null,"~ 15.6 ppm product by vol results in theoretical of\n~ 1.4 ppm as total Cl2\n(3.2 total Br2) ","1-4 total Cl2\n(2.3-9 ppm total Br2)","2010-08-27"]
[]
["*NPIRS Database"]
["**  These products are all mixtures of several inorganic salts.  "]
["***% by weight per product label.  Products contain stabilizers that may not be reflected in the composition listed on the label."]
["#   I: Initial Dose; M: Maintenance Dose, both as product"]